## Sc.B (Lift)
Construction of Shaheed Mohtarma Benazir Bhutto Charity Hospital at Mirpurkhas City. (Installation of Stretcher Lift 1000-Kg)
Schedule "B".
Sr. No: | Items of Work. |  | Qty: |  | Rate. | Unit. | Amount.
| Providing of fully imported Hospital Stretcher lift complete in all respects with the following technical specifications. |  | 1 | -No. |  | Each.
| Make. | Kone / Hyundai / Mitsubishi / Fuji / Otis / Schindler or equivalent.
| Country of Origion. | China / Korea.
| Type. | Hospital Stretcher Lift.
| Load Capacity. | 750-Kg (08-Persons)
| Speed. | 1.0 Meter per second.
| Car Travel. | 26 Ft'
| Floor served / No of Stops. | Ground, Ist, 2nd Floor (3-stops)
| Position of Stop. | In Line.
| Control System. | V V V F microprocessor with A.C. drive.
| Operating System. | Simplex, Full Selective Collective Control.
Car Design.
| Finish front wall. | Stainless steel.
| Finish rear and side walls. | Stainless steel.
| Finish car door panels. | Stainless steel.
| Car door sills. | Aluminium.
| Flooring. | Granite, Shade and Colour as approved.
| Ceiling. | With modular light fitting.
| Dimansions inside Cabin. | Width = 1400 mm Depth = 2200 mm Height = 2400 mm
Door.
| Type. | Automatic Two Penal Centre Opening.
| Door finish. | Satin / hairline stainless steel.
| Door Dimansions clear. | Width = 1000 mm Height = 2100 mm
Mechanical Equipment.
| Supension ropes. | Included.
| Guide rails and brackers. | Included.
| Buffers. | Included.
| Counter weight. | Included complete with blocks.
Hoist way.
| Type. | Concrete / Steel Structure partialy.
| Machine room location. | Top roof / Machine Room less.
| Inside Dimansion. | Suitable space available at site.
| Pit depth. | 1500 mm.
| Main Power Supply. | 3 Phase, 380~415 Volts, 50 Hz ± 5%.
Special Features.
| (a) | Car Direction / Position indicator.
| (b) | Emergency Operation.
| (c) | Car Light.
| (d) | Door Open button.
| (e) | Emergency Alarm.
| (f) | Fan.
| (g) | Intercom unit.
| (h) | Full height infra red light Door protection.
| (i) | Overlaod device & phase Protection.
| (j) | Fireman switch.
| (k) | UPS backup.
2 | Installation, connecting, testing and commissioning of above lift complete in all respect including allied civil work up to entire satisfaction of Engineer Incharge. |  | 1 | -Job. |  | P.Job
3 | Conversion of existing open space into lift well by carryout all necessary Civil work and fabricating steel structure frame work required for completion of lift well which include cutting, welding, masonry work, plastering, dismantling of windows frame to make access and making pit etc i/c making good damages complete in all respect as per instruction of Engineer Incharge and as requirement of safety standard. |  | 1 | -Job. |  | P.Job
4 | Providing & laying 4 core, 25 mm, PVC insulated & PVC sheathed, 600 / 1000 Volts grade with standard copper conductor, un armored, L.T. cable in existing all kind of conducit or cable duct as per P.W.D. specification as required. |  | 25 | -Mtrs: |  | P.Mtrs.
5 | Supply & drawing of 10 mm, single core, PVC insulated wire in all kinds of existing or given conduit / cable duct as required. |  | 25 | -Mtrs: |  | P.Mtrs.
6 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing, vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC. PVC wire complete as required. |  | 6 | -Sft: |  | P.Sft:
7 | Providing & fixing 15 to 60 Amps (Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, i/c inter-connection as required. |  | 1 | -No. |  | Each.
T o t a l :-
Sub-Engineer Buildings Sub-Division Mirpurkhas |  | Assistant Engineer Buildings Sub-Division Mirpurkhas |  |  | Executive Engineer Buildings Division Mirpurkhas