## Landhi
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17, BLOCK-6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI LANDHI HOSPITAL KARACHI
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 30 | Each | 197.795 | 5933.85
| b) First Floor | 30 | Each | 211.61 | 6348.3
| c) Second Floor | 5 | Each | 225.42 | 1127.1
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 30 | Each | 127.075 | 3812.25
| b) First Floor | 30 | Each | 137.58 | 4127.4
| c) Second Floor | 5 | Each | 148.08 | 740.4
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 160 | 100 Cft. | 2773.55 | 4437.68
| b) First Floor | 25 | 100 Cft. | 3024.39 | 756.0975
| c) Second Floor | 275 | 100 Cft. | 3253.68 | 8947.62
| d) Third Floor | 250 | 100 Cft. | 3482.97 | 8707.425
39/123 | Dismantling C.C. floor upto 2" (51 mm) thick in basement, plinth and ground floor including disposing off the material as directed within three chains (91.5 m). | 2500 | 100 Cft. | 494.4875 | 12362.1875
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 350 | 100 Cft. | 988.975 | 3461.4125
| b) First Floor | 350 | 100 Cft. | 1239.82 | 4339.37
| c) Second Floor | 400 | 100 Cft. | 1469.11 | 5876.44
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 10000 | 100 Sq.ft. | 602.78 | 60278
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 650 | 100 Cft | 535.0885 | 3478.0752
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 110 | 100 Cft | 10085.8049 | 11094.3854
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 450 | 100 Cft. | 18172.93 | 81778.185
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 185 | 100 Cft. | 17514.88 | 32402.528
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 350 | 100 Cft. | 22448.44 | 78569.54
| b) First Floor | 550 | 100 Cft. | 23397.64 | 128687.02
| c) Second Floor | 550 | 100 Cft. | 24149.14 | 132820.27
| d) Third Floor | 150 | 100 Cft. | 24900.64 | 37350.96
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 350 | 100 Cft. | 20668.6 | 72340.1
| b) First Floor | 1650 | 100 Cft. | 21617.8 | 356693.7
| c) Second Floor | 2950 | 100 Cft. | 22369.25 | 659892.875
| d) Third Floor | 450 | 100 Cft. | 23120.7 | 104043.15
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 1350 | 100 Cft. | 20143.99 | 271943.865
| b) First Floor | 2550 | 100 Cft. | 21093.19 | 537876.345
| c) Second Floor | 3550 | 100 Cft. | 21844.64 | 775484.72
| d) Third Floor | 650 | 100 Cft. | 22596.09 | 146874.585
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 145 | 100 Cft. | 22538.92 | 32681.434
| b) First Floor | 655 | 100 Cft. | 23488.12 | 153847.186
| c) Second Floor | 950 | 100 Cft. | 24239.57 | 230275.915
50/114 | Providing and laying reinforced cement concrete using 50 %screened graded bajri & 50 % crushed boulder 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2 ) at 28 days with a mix not leaner than 1:2:4 in straight stairs and landing of required section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 50 | 100 Cft. | 25545.28 | 12772.64
| b) First Floor | 50 | 100 Cft. | 26494.48 | 13247.24
| c) Second Floor | 175 | 100 Cft. | 27245.93 | 47680.3775
| d) Third Floor | 275 | 100 Cft. | 27997.38 | 76992.795
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 225 | 100 Cft. | 25857.43 | 58179.2175
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 2500 | 100 Cft. | 15033.28 | 375832
| b) First Floor | 3500 | 100 Cft. | 15857.05 | 554996.75
| c) Second Floor | 4580 | 100 Cft. | 16536.53 | 757373.074
| d) Third Floor | 680 | 100 Cft. | 16536.53 | 112448.404
2/122 | 1/4" (6.4 mm) thick cement plaster 1:4 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 450 | 100 Sq.ft. | 1625.9797 | 7316.9088
| b) First Floor | 4500 | 100 Sq.ft. | 1779.85 | 80093.25
| c) Second Floor | 8500 | 100 Sq.ft. | 1910.31 | 162376.35
| d) Third Floor | 850 | 100 Sq.ft. | 2040.77 | 17346.545
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 1800 | 100 Sq.ft. | 1730.7392 | 31153.3053
| b) First Floor | 1500 | 100 Sq.ft. | 1884.61 | 28269.15
| c) Second Floor | 10500 | 100 Sq.ft. | 2015.07 | 211582.35
| d) Third Floor | 3500 | 100 Sq.ft. | 2145.53 | 75093.55
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 2000 | 100 Sq.ft | 2204.0168 | 44080.3355
| b) First Floor | 3500 | 100 Sq.ft | 2328.9 | 81511.5
| c) Second Floor | 600 | 100 Sq.ft | 2406.95 | 14441.7
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 1000 | 100 Sq.ft | 3075.7 | 30757
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 75 | Cft. | 4595.1353 | 344635.1469
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 350 | Sft. | 571.6761 | 200086.6296
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required. | 25 | Sft. | 551.814 | 13795.3498
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required. | 150 | Sq ft | 303.1167 | 45467.5104
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required. | 65 | Sq ft | 503.6173 | 32735.1229
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required. | 220 | Sq ft | 419.1321 | 92209.0715
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 675 | Sq ft | 91.9382 | 62058.2651
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required. | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 125 | Sft | 327.3112 | 40913.9046
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 5000 | 100 Sq.ft | 124.434 | 6221.7
151/122 | Distempering with vinyle distemper (ICI) Dulux Paintex of approved make and shade in two coats over and including the cost of one priming coat of lime wash including sand papering, dusting, and filling the holes, cracks and inequalities, if any, at any height in any floor. | 10000 | 100 Sq.ft | 1053.5412 | 105354.12
162/122 | Painting with (ICI) Dulux plastic emulsion paint VIP of approved shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor . | 10500 | 100 Sq.ft | 2742.0796 | 287918.358
160/122 | Painting wood work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 450 | 100 Sq.ft | 2585.2182 | 11633.482
159/122 | Painting iron work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 150 | 100 Sq.ft | 2776.6219 | 4164.9329
172/122 | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | 6500 | 100 Sq.ft | 1406.8847 | 91447.5055
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 125000 | 100 Sq.ft. | 560.9844 | 701230.4688
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 150000 | 100 Sq.ft. | 505.095 | 757642.5
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 2500 | 100 Sq.ft. | 924.3325 | 23108.3125
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1850 | 100 Sq.ft. | 955.7145 | 17680.7183
99/119 | Providing and fixing fully glazed Bronze anodized or powder coated aluminium Sliding windows as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators) deluxe model box section 95mm x 30mm and 1.6mm thick including the cost of aluminium netting ,fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 750 | Sq.ft. | 567.543 | 425657.2503
108/119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Hinged door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators), Economy model section, 76.2mm x 30mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 250 | Sq.ft. | 440.7402 | 110185.0612
120 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 1100 | Sq.ft. | 106.1059 | 116716.4427
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 3500 | 100 Sq.ft. | 3053.2494 | 106863.7298
157 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 500 | Sft | 74.8883 | 37444.153
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 1450 | 100 Rft. | 1368.1642 | 19838.3805
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors. | 1480 | Sq.ft. | 103.0965 | 152582.82
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor. | 80 | Sqft | 363.11 | 29048.796
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 18 | Cwt | 9607.9425 | 172942.9642
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 350 | 100 Sq.ft | 12123.2262 | 42431.2917
| b) First Floor | 450 | 100 Sq.ft | 12365.19 | 55643.355
| c) Second Floor | 430 | 100 Sq.ft | 12653.98 | 54412.114
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 450 | 100 Sq.ft | 8408.2262 | 37837.0177
| b) First Floor | 870 | 100 Sq.ft | 8650.19 | 75256.653
| c) Second Floor | 850 | 100 Sq.ft | 8938.98 | 75981.33
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension. | 6 | Cwt. | 6249.9391 | 37499.6344
| b) First Floor | 80 | Cwt. | 6323.42 | 505873.6
| c) Second Floor | 260 | Cwt. | 6396.9 | 1663194
| d) Third Floor | 40 | Cwt. | 6470.38 | 258815.2
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/25 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | 250 | Sq.ft. | 494.9753 | 123743.8291
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 20 | Cwt. | 7634.0786 | 152681.5726
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 30 | Each | 2531.555 | 75946.65
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 20 | Each | 1063.8056 | 21276.112
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 20 | Each | 88.5392 | 1770.7846
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 45 | Each | 59.6369 | 2683.6582
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 20 | Each | 382.4221 | 7648.4417
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 140 | Rft. | 121.8152 | 17054.128
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 12 | Each | 2420.5025 | 29046.03
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 4 | Each | 407.2754 | 1629.1015
3 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent. | 20000 | 100 Sq.ft. | 2659.7875 | 531957.4913
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 1250 | Ib | 145.396 | 181745
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete. | 25 | Rft. | 107.7375 | 2693.4375
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete | 550 | Rft. | 210.5485 | 115801.6979
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 40 | Each | 159.1642 | 6366.568
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 25 | Each | 629.85 | 15746.25
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 30 | Lbs. | 66.0667 | 1982.0017
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 850 | % Cft | 42.3057 | 359.5986
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor. | 650 | 100 Sq.ft. | 1878.9641 | 12213.2666
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors. | 600 | Rft. | 9.6687 | 5801.25
63/117 | Providing and laying floor of 6mm (approx: 1/4") thick coloured glazed tiles 12" x 12" (304mm x 304mm) of master make (Pakistani) first grade in ground floor laid over 1" (25mm) thick cement mortar 1:2 (1 cement and 2 sand) including jointing and washing the tiles with white cement slurry a matching colour (by using pigment in white cement) and curing etc. complete. | 5500 | 100 Sq.ft. | 18359.6026 | 1009778.1429
| b) First Floor | 4500 | 100 Sq.ft. | 18554.73 | 834962.85
| c) Second Floor | 1500 | 100 Sq.ft. | 18683.51 | 280252.65
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 25 | Each | 54.36 | 1359
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 15 | Each | 84.74 | 1271.1
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 20 | cwt | 7997.6 | 159952
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 50 | rft | 333.08 | 16654
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete. | 6 | cwt | 6074.4 | 36446.4
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 45 | Sqft | 225.13 | 10130.85
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor. | 85 | 100Rft | 2258.58 | 1919.793
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 850 | 100 Sq.ft | 135.06 | 1148.01
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 1150 | 100 Sq.ft | 284.54 | 3272.21
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 1500 | 100 Sq.ft | 2371.9061 | 35578.5908
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 550 | 100 Sft | 727.47 | 4001.085
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 2500 | Sft | 71.69 | 179225
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 30 | lbs | 180.48 | 5414.4
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 1000 | 100 Sft. | 9097.3098 | 90973.0975
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 2500 | 100 Sq.ft | 43.4293 | 1085.7313
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 2450 | 100 Sq.ft | 110.385 | 2704.4325
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete. | 20 | cwt | 5988.48 | 119769.6
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 30000 | 100 Sq.ft. | 139.9325 | 41979.75
30/125 | Plastering 1" (25 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 1500 | 100 Sq.ft. | 2986.91 | 44803.65
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 350 | SQFT | 48.02 | 16807
| TOTAL OF SUB -HEAD A |  |  |  | 17949079.8494
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI LANDHI HOSPITAL KARACHI
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 650 | 100 Sq.ft. | 3840.8809 | 24965.7261
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 45 | 100 Sq ft | 12266.26 | 5519.817
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 6500 | 100 Sqft | 6102.5179 | 396663.666
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 460 | 100 Rft. | 13968.6715 | 64255.8888
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 5600 | 100 Cft | 2823.86 | 158136.16
| TOTAL OF SUB HEAD B |  |  |  | 649541.2578
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI LANDHI HOSPITAL KARACHI
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4. | 20 | Each | 3424.916 | 68498.32
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 20 | Each | 4601.3 | 92026
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4. | 25 | Each | 4628.14 | 115703.5
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 25 | Each | 863.83 | 21595.75
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 10 | Each | 12406.768 | 124067.68
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 85 | Each | 389.752 | 33128.92
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 10 | Each | 6611.132 | 66111.32
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 10 | Each | 968.44 | 9684.4
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
10/302 | Providing and fixing bath room accessories of set of 7 pieces consist of one cosmatic shelf, one towel rod with bracket, one soap dish, one tooth brush holder with glass and cover, one tissue paper holder one double hook one towel ring etc complete of approved quality as per direction of Engineer in-charge. | 0 | Each | 3986.62 | 0
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 35 | Each | 279.75 | 9791.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 2 | Each | 66891 | 133782
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 250 | Rft | 68.32 | 17080
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 55 | Rft | 85.26 | 4689.3
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 45 | Rft | 120.35 | 5415.75
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 30 | Rft | 158.07 | 4742.1
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 155 | Rft | 35.21 | 5457.55
| Do. Do. 1 inch (25mm) dia. | 175 | Rft | 42.23 | 7390.25
| Do. Do. 1-1/4 inch (32 mm) dia.. | 225 | Rft | 64.23 | 14451.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 350 | Rft | 82.1 | 28735
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 550 | R.ft | 67.8153 | 37298.3952
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 150 | R.ft | 88.2753 | 13241.2896
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 560 | R.ft | 127.734 | 71531.0534
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 35 | Each | 882.9832 | 30904.412
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 10 | Each | 17442.4785 | 174424.7846
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52m) and lead up to one chain (30.48 m) | 3500 | %Cft | 599.7012 | 20989.5413
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm) dia. pipe. | 350 | R.ft. | 250.26 | 87591
311/1 | Providing and fixing bath room accessories of set of 7 pieces consist of one cosmatic shelf, one towel rod with bracket, one soap dish, one tooth brush holder with glass and cover, one tissue paper holder one double hook one towel ring etc complete of approved quality as per direction of Engineer in-charge. | 15 | Each | 3986.62 | 59799.3
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 35 | Each | 720.94 | 25232.9
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 17 | Each | 1500 | 25500
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 12 | Each | 105 | 1260
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 12 | Each | 125 | 1500
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 12 | Each | 215 | 2580
| PPRC Ball Valve 20 mm. | 12 | Each | 643.5 | 7722
| PPRC Ball Valve 25 mm. | 12 | Each | 783.75 | 9405
| TOTAL OF SUB HEAD C |  |  |  | 1383171.9942
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI LANDHI HOSPITAL KARACHI
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 4 | Each | 4500 | 18000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 1200 | Rft | 25 | 30000
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 450 | 100 Sq.ft. | 12000 | 54000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 250 | Sft | 700 | 175000
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 1250 | Rft | 140 | 175000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 1250 | Rft | 225 | 281250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 80 | R.ft | 200.08 | 16006.4
| 8 inch dia | 50 | R.ft | 352.16 | 17608
| 12 inch dia | 50 | R.ft | 719.35 | 35967.5
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 2000 | Sft | 10 | 20000
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 30500 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 100 | Rft | 310 | 31000
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 4 | No | 350 | 1400
| Total Of Non Schedule Items |  |  |  | 937731.9
SUMMARY
| Total of Sub Head 'A' | 17949079.8494
| Total of Sub Head 'B' | 649541.2578
| Total of Sub Head 'C' | 1383171.9942
| Total of Non-Schedule Items | 937731.9
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 20919525.0014

## Over Head Tank
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI LANDHI HOSPITAL KARACHI (OVER HEAD WATER TANK)
SUB -HEAD (A ) CIVIL WORKS ( Special Repair )
Schedule Item based on Pak PWD Schedule of Rates 2012
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
1 | Proping and supporting Structural member and its adjoining areas with adjustable steel props ( Scaffoling pipes )and joints 5 Mtons capacity bracing steel /timber runners to relive the structural member of the reqired load coming over it as per design submitted by the Contractor and approved by the engineer Incharge. The height of the Prop complete as per required | 1 | job | 50000 | 50000
2 | Providing and fixing temporary engineered tubular standard double scaffolding system on exterior side maintaining it in a serviceable condition till completion of the work and removing it thereafter.The scaffolding system shall be stiffened with bracings, runners,connecting with the building etc with suitable platform at required locations with essential safety feature for the workers etc. complete as per direction of the Engineer Incharge. | 1 | Each | 40000 | 40000
3 | Providing and erecting and removing safety screen made of Wooven PVC temporary Screen with all necessary fixing arrangement to ensure that it will remain in position till completion of job or as per direction of Engineer Incharge | 1 | Each | 8000 | 8000
4 | Chipping off unsound /unworkable concrete with chiesel and hammer including brushing with steel wire brush to remove rust and dust and disposal of debris within a range of 50m as per direction of Engineer Incharge complete.
| a) For slabs upto average 25mm thick | 20 | Sqm | 120 | 2400
| b) For beams and columns average 25mm ~ 75mm thick | 30 | Sqm | 250 | 7500
5 | Cutting Reinforcement bars in RCC carefully not damaging any other structure dia upto 25mm | 22 | Each | 25 | 550
6 | Cleaning reinforcement of total rust using manually by wire brush including from the behind from reinforcement to give a clean surface. For measurement length of the bar shall be taken. | 260 | m | 6 | 1560
7 | Inserting new reinforcement bar for making structural connection in RCC beams /slabs/columns by using drill machine by drilling hole upto 200mm fixing reinforcement bar in position by using concrete epoxy complete including cleaning the dust etc complete.
| a) For steel bar 12mm dia | 70 | Each | 250 | 17500
| b) For steel bar 20mm dia | 50 | Each | 350 | 17500
8 | Providing and fixing MS shear Key by drilling in existing RCC for shortcrete including cleaning the dust etc complete
| a) 12mm dia 150mm long | 70 | Each | 350 | 24500
9 | Providing mixing and applying modified Cement mortar MS shear Key by drilling in existing RCC for shortcrete including cleaning the dust etc complete
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 350 | 100 Cft. | 988.975 | 3461.4125
| b) First Floor | 350 | 100 Cft. | 1239.82 | 4339.37
| c) Second Floor | 400 | 100 Cft. | 1469.11 | 5876.44
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 10000 | 100 Sq.ft. | 602.78 | 60278
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 650 | 100 Cft | 535.0885 | 3478.0752
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 110 | 100 Cft | 10085.8049 | 11094.3854
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 450 | 100 Cft. | 18172.93 | 81778.185
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 185 | 100 Cft. | 17514.88 | 32402.528
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 350 | 100 Cft. | 22448.44 | 78569.54
| b) First Floor | 550 | 100 Cft. | 23397.64 | 128687.02
| c) Second Floor | 550 | 100 Cft. | 24149.14 | 132820.27
| d) Third Floor | 150 | 100 Cft. | 24900.64 | 37350.96
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 350 | 100 Cft. | 20668.6 | 72340.1
| b) First Floor | 1650 | 100 Cft. | 21617.8 | 356693.7
| c) Second Floor | 2950 | 100 Cft. | 22369.25 | 659892.875
| d) Third Floor | 450 | 100 Cft. | 23120.7 | 104043.15
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 1350 | 100 Cft. | 20143.99 | 271943.865
| b) First Floor | 2550 | 100 Cft. | 21093.19 | 537876.345
| c) Second Floor | 3550 | 100 Cft. | 21844.64 | 775484.72
| d) Third Floor | 650 | 100 Cft. | 22596.09 | 146874.585
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 145 | 100 Cft. | 22538.92 | 32681.434
| b) First Floor | 655 | 100 Cft. | 23488.12 | 153847.186
| c) Second Floor | 950 | 100 Cft. | 24239.57 | 230275.915
50/114 | Providing and laying reinforced cement concrete using 50 %screened graded bajri & 50 % crushed boulder 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2 ) at 28 days with a mix not leaner than 1:2:4 in straight stairs and landing of required section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 50 | 100 Cft. | 25545.28 | 12772.64
| b) First Floor | 50 | 100 Cft. | 26494.48 | 13247.24
| c) Second Floor | 175 | 100 Cft. | 27245.93 | 47680.3775
| d) Third Floor | 275 | 100 Cft. | 27997.38 | 76992.795
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 225 | 100 Cft. | 25857.43 | 58179.2175
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 2500 | 100 Cft. | 15033.28 | 375832
| b) First Floor | 3500 | 100 Cft. | 15857.05 | 554996.75
| c) Second Floor | 4580 | 100 Cft. | 16536.53 | 757373.074
| d) Third Floor | 680 | 100 Cft. | 16536.53 | 112448.404
2/122 | 1/4" (6.4 mm) thick cement plaster 1:4 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 450 | 100 Sq.ft. | 1625.9797 | 7316.9088
| b) First Floor | 4500 | 100 Sq.ft. | 1779.85 | 80093.25
| c) Second Floor | 8500 | 100 Sq.ft. | 1910.31 | 162376.35
| d) Third Floor | 850 | 100 Sq.ft. | 2040.77 | 17346.545
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 1800 | 100 Sq.ft. | 1730.7392 | 31153.3053
| b) First Floor | 1500 | 100 Sq.ft. | 1884.61 | 28269.15
| c) Second Floor | 10500 | 100 Sq.ft. | 2015.07 | 211582.35
| d) Third Floor | 3500 | 100 Sq.ft. | 2145.53 | 75093.55
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 2000 | 100 Sq.ft | 2204.0168 | 44080.3355
| b) First Floor | 3500 | 100 Sq.ft | 2328.9 | 81511.5
| c) Second Floor | 600 | 100 Sq.ft | 2406.95 | 14441.7
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 1000 | 100 Sq.ft | 3075.7 | 30757
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 75 | Cft. | 4595.1353 | 344635.1469
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 350 | Sft. | 571.6761 | 200086.6296
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 25 | Sft. | 551.814 | 13795.3498
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 150 | Sq ft | 303.1167 | 45467.5104
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 65 | Sq ft | 503.6173 | 32735.1229
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 220 | Sq ft | 419.1321 | 92209.0715
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 675 | Sq ft | 91.9382 | 62058.2651
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 125 | Sft | 327.3112 | 40913.9046
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 5000 | 100 Sq.ft | 124.434 | 6221.7
151/122 | Distempering with vinyle distemper (ICI) Dulux Paintex of approved make and shade in two coats over and including the cost of one priming coat of lime wash including sand papering, dusting, and filling the holes, cracks and inequalities, if any, at any height in any floor. | 10000 | 100 Sq.ft | 1053.5412 | 105354.12
162/122 | Painting with (ICI) Dulux plastic emulsion paint VIP of approved shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor . | 10500 | 100 Sq.ft | 2742.0796 | 287918.358
160/122 | Painting wood work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 450 | 100 Sq.ft | 2585.2182 | 11633.482
159/122 | Painting iron work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 150 | 100 Sq.ft | 2776.6219 | 4164.9329
172/122 | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | 6500 | 100 Sq.ft | 1406.8847 | 91447.5055
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 125000 | 100 Sq.ft. | 560.9844 | 701230.4688
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 150000 | 100 Sq.ft. | 505.095 | 757642.5
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 2500 | 100 Sq.ft. | 924.3325 | 23108.3125
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1850 | 100 Sq.ft. | 955.7145 | 17680.7183
99/119 | Providing and fixing fully glazed Bronze anodized or powder coated aluminium Sliding windows as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators) deluxe model box section 95mm x 30mm and 1.6mm thick including the cost of aluminium netting ,fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 750 | Sq.ft. | 567.543 | 425657.2503
108/119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Hinged door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators), Economy model section, 76.2mm x 30mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 250 | Sq.ft. | 440.7402 | 110185.0612
120 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 1100 | Sq.ft. | 106.1059 | 116716.4427
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 3500 | 100 Sq.ft. | 3053.2494 | 106863.7298
157 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 500 | Sft | 74.8883 | 37444.153
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 1450 | 100 Rft. | 1368.1642 | 19838.3805
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 1480 | Sq.ft. | 103.0965 | 152582.82
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 80 | Sqft | 363.11 | 29048.796
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 18 | Cwt | 9607.9425 | 172942.9642
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 350 | 100 Sq.ft | 12123.2262 | 42431.2917
| b) First Floor | 450 | 100 Sq.ft | 12365.19 | 55643.355
| c) Second Floor | 430 | 100 Sq.ft | 12653.98 | 54412.114
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 450 | 100 Sq.ft | 8408.2262 | 37837.0177
| b) First Floor | 870 | 100 Sq.ft | 8650.19 | 75256.653
| c) Second Floor | 850 | 100 Sq.ft | 8938.98 | 75981.33
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 6 | Cwt. | 6249.9391 | 37499.6344
| b) First Floor | 80 | Cwt. | 6323.42 | 505873.6
| c) Second Floor | 260 | Cwt. | 6396.9 | 1663194
| d) Third Floor | 40 | Cwt. | 6470.38 | 258815.2
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/25 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor.. | 250 | Sq.ft. | 494.9753 | 123743.8291
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 20 | Cwt. | 7634.0786 | 152681.5726
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 30 | Each | 2531.555 | 75946.65
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 20 | Each | 1063.8056 | 21276.112
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 20 | Each | 88.5392 | 1770.7846
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 45 | Each | 59.6369 | 2683.6582
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 20 | Each | 382.4221 | 7648.4417
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 140 | Rft. | 121.8152 | 17054.128
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 12 | Each | 2420.5025 | 29046.03
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 4 | Each | 407.2754 | 1629.1015
3 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 20000 | 100 Sq.ft. | 2659.7875 | 531957.4913
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 1250 | Ib | 145.396 | 181745
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 25 | Rft. | 107.7375 | 2693.4375
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 550 | Rft. | 210.5485 | 115801.6979
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 40 | Each | 159.1642 | 6366.568
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 25 | Each | 629.85 | 15746.25
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 30 | Lbs. | 66.0667 | 1982.0017
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 850 | % Cft | 42.3057 | 359.5986
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 650 | 100 Sq.ft. | 1878.9641 | 12213.2666
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 600 | Rft. | 9.6687 | 5801.25
63/117 | Providing and laying floor of 6mm (approx: 1/4") thick coloured glazed tiles 12" x 12" (304mm x 304mm) of master make (Pakistani) first grade in ground floor laid over 1" (25mm) thick cement mortar 1:2 (1 cement and 2 sand) including jointing and washing the tiles with white cement slurry a matching colour (by using pigment in white cement) and curing etc. complete. | 5500 | 100 Sq.ft. | 18359.6026 | 1009778.1429
| b) First Floor | 4500 | 100 Sq.ft. | 18554.73 | 834962.85
| c) Second Floor | 1500 | 100 Sq.ft. | 18683.51 | 280252.65
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 25 | Each | 54.36 | 1359
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 15 | Each | 84.74 | 1271.1
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 20 | cwt | 7997.6 | 159952
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 50 | rft | 333.08 | 16654
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 6 | cwt | 6074.4 | 36446.4
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 45 | Sqft | 225.13 | 10130.85
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 85 | 100Rft | 2258.58 | 1919.793
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 850 | 100 Sq.ft | 135.06 | 1148.01
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 1150 | 100 Sq.ft | 284.54 | 3272.21
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 1500 | 100 Sq.ft | 2371.9061 | 35578.5908
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 550 | 100 Sft | 727.47 | 4001.085
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 2500 | Sft | 71.69 | 179225
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 30 | lbs | 180.48 | 5414.4
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 1000 | 100 Sft. | 9097.3098 | 90973.0975
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 2500 | 100 Sq.ft | 43.4293 | 1085.7313
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 2450 | 100 Sq.ft | 110.385 | 2704.4325
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 20 | cwt | 5988.48 | 119769.6
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 30000 | 100 Sq.ft. | 139.9325 | 41979.75
30/125 | Plastering 1" (25 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 1500 | 100 Sq.ft. | 2986.91 | 44803.65
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 350 | SQFT | 48.02 | 16807
| TOTAL OF SUB -HEAD A |  |  |  | 18011289.5394
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI LANDHI HOSPITAL KARACHI
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 650 | 100 Sq.ft. | 3840.8809 | 24965.7261
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 45 | 100 Sq ft | 12266.26 | 5519.817
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 6500 | 100 Sqft | 6102.5179 | 396663.666
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 460 | 100 Rft. | 13968.6715 | 64255.8888
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 5600 | 100 Cft | 2823.86 | 158136.16
| TOTAL OF SUB HEAD B |  |  |  | 649541.2578
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI LANDHI HOSPITAL KARACHI
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4.. | 20 | Each | 3424.916 | 68498.32
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4.. | 20 | Each | 4601.3 | 92026
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4.. | 25 | Each | 4628.14 | 115703.5
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 25 | Each | 863.83 | 21595.75
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 10 | Each | 12406.768 | 124067.68
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 85 | Each | 389.752 | 33128.92
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 10 | Each | 6611.132 | 66111.32
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 10 | Each | 968.44 | 9684.4
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
10/302 | Providing and fixing bath room accessories of set of 7 pieces consist of one cosmatic shelf, one towel rod with bracket, one soap dish, one tooth brush holder with glass and cover, one tissue paper holder one double hook one towel ring etc complete of approved quality as per direction of Engineer in-charge. | 0 | Each | 3986.62 | 0
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 35 | Each | 279.75 | 9791.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 2 | Each | 66891 | 133782
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 250 | Rft | 68.32 | 17080
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 55 | Rft | 85.26 | 4689.3
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 45 | Rft | 120.35 | 5415.75
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 30 | Rft | 158.07 | 4742.1
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 155 | Rft | 35.21 | 5457.55
| Do. Do. 1 inch (25mm) dia. | 175 | Rft | 42.23 | 7390.25
| Do. Do. 1-1/4 inch (32 mm) dia.. | 225 | Rft | 64.23 | 14451.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 350 | Rft | 82.1 | 28735
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 550 | R.ft | 67.8153 | 37298.3952
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 150 | R.ft | 88.2753 | 13241.2896
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 560 | R.ft | 127.734 | 71531.0534
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 35 | Each | 882.9832 | 30904.412
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 10 | Each | 17442.4785 | 174424.7846
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 3500 | %Cft | 599.7012 | 20989.5413
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe.. | 350 | R.ft. | 250.26 | 87591
311/1 | Providing and fixing bath room accessories of set of 7 pieces consist of one cosmatic shelf, one towel rod with bracket, one soap dish, one tooth brush holder with glass and cover, one tissue paper holder one double hook one towel ring etc complete of approved quality as per direction of Engineer in-charge. | 15 | Each | 3986.62 | 59799.3
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 35 | Each | 720.94 | 25232.9
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 17 | Each | 1500 | 25500
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 12 | Each | 105 | 1260
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 12 | Each | 125 | 1500
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 12 | Each | 215 | 2580
| PPRC Ball Valve 20 mm. | 12 | Each | 643.5 | 7722
| PPRC Ball Valve 25 mm. | 12 | Each | 783.75 | 9405
| TOTAL OF SUB HEAD C |  |  |  | 1383171.9942
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI LANDHI HOSPITAL KARACHI
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 4 | Each | 4500 | 18000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 1200 | Rft | 25 | 30000
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 450 | 100 Sq.ft. | 12000 | 54000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 250 | Sft | 700 | 175000
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 1250 | Rft | 140 | 175000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 1250 | Rft | 225 | 281250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 80 | R.ft | 200.08 | 16006.4
| 8 inch dia | 50 | R.ft | 352.16 | 17608
| 12 inch dia | 50 | R.ft | 719.35 | 35967.5
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 2000 | Sft | 10 | 20000
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 30500 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 100 | Rft | 310 | 31000
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 4 | No | 350 | 1400
| Total Of Non Schedule Items |  |  |  | 937731.9
SUMMARY
| Total of Sub Head 'A' | 18011289.5394
| Total of Sub Head 'B' | 649541.2578
| Total of Sub Head 'C' | 1383171.9942
| Total of Non-Schedule Items | 937731.9
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 20981734.6914

## valika hospital
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( MAIN HOSPITAL)
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 15 | Each | 197.795 | 2966.925
| b) First Floor | 20 | Each | 211.61 | 4232.2
| c) Second Floor | 5 | Each | 225.42 | 1127.1
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 15 | Each | 127.075 | 1906.125
| b) First Floor | 20 | Each | 137.58 | 2751.6
| c) Second Floor | 5 | Each | 148.08 | 740.4
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 20 | 100 Cft. | 2773.55 | 554.71
| b) First Floor | 20 | 100 Cft. | 3024.39 | 604.878
| c) Second Floor | 150 | 100 Cft. | 3253.68 | 4880.52
| d) Third Floor | 250 | 100 Cft. | 3482.97 | 8707.425
39/123 | Dismantling C.C. floor upto 2" (51 mm) thick in basement, plinth and ground floor including disposing off the material as directed within three chains (91.5 m). | 150 | 100 Cft. | 494.4875 | 741.7313
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 60 | 100 Cft. | 988.975 | 593.385
| b) First Floor | 120 | 100 Cft. | 1239.82 | 1487.784
| c) Second Floor | 200 | 100 Cft. | 1469.11 | 2938.22
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 25000 | 100 Sq.ft. | 602.78 | 150695
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 50 | 100 Cft | 535.0885 | 267.5442
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 50 | 100 Cft | 10085.8049 | 5042.9024
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 450 | 100 Cft. | 18172.93 | 81778.185
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 25 | 100 Cft. | 17514.88 | 4378.72
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 10 | 100 Cft. | 22448.44 | 2244.844
| b) First Floor | 10 | 100 Cft. | 23397.64 | 2339.764
| c) Second Floor | 10 | 100 Cft. | 24149.14 | 2414.914
| d) Third Floor | 10 | 100 Cft. | 24900.64 | 2490.064
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 25 | 100 Cft. | 20668.6 | 5167.15
| b) First Floor | 60 | 100 Cft. | 21617.8 | 12970.68
| c) Second Floor | 120 | 100 Cft. | 22369.25 | 26843.1
| d) Third Floor | 180 | 100 Cft. | 23120.7 | 41617.26
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 50 | 100 Cft. | 20143.99 | 10071.995
| b) First Floor | 60 | 100 Cft. | 21093.19 | 12655.914
| c) Second Floor | 280 | 100 Cft. | 21844.64 | 61164.992
| d) Third Floor | 350 | 100 Cft. | 22596.09 | 79086.315
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 145 | 100 Cft. | 22538.92 | 32681.434
| b) First Floor | 655 | 100 Cft. | 23488.12 | 153847.186
| c) Second Floor | 1250 | 100 Cft. | 24239.57 | 302994.625
50/114 | Providing and laying reinforced cement concrete using 50 %screened graded bajri & 50 % crushed boulder 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2 ) at 28 days with a mix not leaner than 1:2:4 in straight stairs and landing of required section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 20 | 100 Cft. | 25545.28 | 5109.056
| b) First Floor | 50 | 100 Cft. | 26494.48 | 13247.24
| c) Second Floor | 150 | 100 Cft. | 27245.93 | 40868.895
| d) Third Floor | 150 | 100 Cft. | 27997.38 | 41996.07
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 650 | 100 Cft. | 25857.43 | 168073.295
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 40 | 100 Cft. | 15033.28 | 6013.312
| b) First Floor | 60 | 100 Cft. | 15857.05 | 9514.23
| c) Second Floor | 120 | 100 Cft. | 16536.53 | 19843.836
| d) Third Floor | 120 | 100 Cft. | 16536.53 | 19843.836
2/122 | 1/4" (6.4 mm) thick cement plaster 1:4 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 150 | 100 Sq.ft. | 1625.9797 | 2438.9696
| b) First Floor | 180 | 100 Sq.ft. | 1779.85 | 3203.73
| c) Second Floor | 180 | 100 Sq.ft. | 1910.31 | 3438.558
| d) Third Floor | 120 | 100 Sq.ft. | 2040.77 | 2448.924
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 360 | 100 Sq.ft. | 1730.7392 | 6230.6611
| b) First Floor | 360 | 100 Sq.ft. | 1884.61 | 6784.596
| c) Second Floor | 340 | 100 Sq.ft. | 2015.07 | 6851.238
| d) Third Floor | 250 | 100 Sq.ft. | 2145.53 | 5363.825
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 460 | 100 Sq.ft | 2204.0168 | 10138.4772
| b) First Floor | 1250 | 100 Sq.ft | 2328.9 | 29111.25
| c) Second Floor | 1650 | 100 Sq.ft | 2406.95 | 39714.675
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 1000 | 100 Sq.ft | 3075.7 | 30757
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 35 | Cft. | 4595.1353 | 160829.7352
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 120 | Sft. | 571.6761 | 68601.1301
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 50 | Sft. | 551.814 | 27590.6996
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 100 | Sq ft | 303.1167 | 30311.6736
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 65 | Sq ft | 503.6173 | 32735.1229
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 150 | Sq ft | 419.1321 | 62869.8214
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 170 | Sq ft | 91.9382 | 15629.489
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 50 | Sft | 327.3112 | 16365.5619
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 5000 | 100 Sq.ft | 124.434 | 6221.7
151/122 | Distempering with vinyle distemper (ICI) Dulux Paintex of approved make and shade in two coats over and including the cost of one priming coat of lime wash including sand papering, dusting, and filling the holes, cracks and inequalities, if any, at any height in any floor. | 850 | 100 Sq.ft | 1053.5412 | 8955.1002
162/122 | Painting with (ICI) Dulux plastic emulsion paint VIP of approved shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor . | 850 | 100 Sq.ft | 2742.0796 | 23307.6766
160/122 | Painting wood work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 60 | 100 Sq.ft | 2585.2182 | 1551.1309
159/122 | Painting iron work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 40 | 100 Sq.ft | 2776.6219 | 1110.6488
172/122 | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | 120 | 100 Sq.ft | 1406.8847 | 1688.2616
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 50000 | 100 Sq.ft. | 560.9844 | 280492.1875
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 50000 | 100 Sq.ft. | 505.095 | 252547.5
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 2500 | 100 Sq.ft. | 924.3325 | 23108.3125
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1850 | 100 Sq.ft. | 955.7145 | 17680.7183
99/119 | Providing and fixing fully glazed Bronze anodized or powder coated aluminium Sliding windows as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators) deluxe model box section 95mm x 30mm and 1.6mm thick including the cost of aluminium netting ,fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 80 | Sq.ft. | 567.543 | 45403.44
108/119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Hinged door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators), Economy model section, 76.2mm x 30mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 80 | Sq.ft. | 440.7402 | 35259.2196
120 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 310 | Sq.ft. | 106.1059 | 32892.8157
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 360 | 100 Sq.ft. | 3053.2494 | 10991.6979
157 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 500 | Sft | 74.8883 | 37444.153
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 1450 | 100 Rft. | 1368.1642 | 19838.3805
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 980 | Sq.ft. | 103.0965 | 101034.57
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 80 | Sqft | 363.11 | 29048.796
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 12 | Cwt | 9607.9425 | 115295.3094
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 50 | 100 Sq.ft | 12123.2262 | 6061.6131
| b) First Floor | 150 | 100 Sq.ft | 12365.19 | 18547.785
| c) Second Floor | 20 | 100 Sq.ft | 12653.98 | 2530.796
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 120 | 100 Sq.ft | 8408.2262 | 10089.8714
| b) First Floor | 560 | 100 Sq.ft | 8650.19 | 48441.064
| c) Second Floor | 260 | 100 Sq.ft | 8938.98 | 23241.348
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 6 | Cwt. | 6249.9391 | 37499.6344
| b) First Floor | 20 | Cwt. | 6323.42 | 126468.4
| c) Second Floor | 60 | Cwt. | 6396.9 | 383814
| d) Third Floor | 40 | Cwt. | 6470.38 | 258815.2
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/25 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | 250 | Sq.ft. | 494.9753 | 123743.8291
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 20 | Cwt. | 7634.0786 | 152681.5726
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 10 | Each | 2531.555 | 25315.55
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 20 | Each | 1063.8056 | 21276.112
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 20 | Each | 88.5392 | 1770.7846
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 45 | Each | 59.6369 | 2683.6582
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 20 | Each | 382.4221 | 7648.4417
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 140 | Rft. | 121.8152 | 17054.128
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 12 | Each | 2420.5025 | 29046.03
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 4 | Each | 407.2754 | 1629.1015
3 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 25000 | 100 Sq.ft. | 2659.7875 | 664946.8642
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 1250 | Ib | 145.396 | 181745
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 25 | Rft. | 107.7375 | 2693.4375
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 550 | Rft. | 210.5485 | 115801.6979
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 40 | Each | 159.1642 | 6366.568
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 25 | Each | 629.85 | 15746.25
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 30 | Lbs. | 66.0667 | 1982.0017
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 850 | % Cft | 42.3057 | 359.5986
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 650 | 100 Sq.ft. | 1878.9641 | 12213.2666
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 600 | Rft. | 9.6687 | 5801.25
63/117 | Providing and laying floor of 6mm (approx: 1/4") thick coloured glazed tiles 12" x 12" (304mm x 304mm) of master make (Pakistani) first grade in ground floor laid over 1" (25mm) thick cement mortar 1:2 (1 cement and 2 sand) including jointing and washing the tiles with white cement slurry a matching colour (by using pigment in white cement) and curing etc. complete. | 1650 | 100 Sq.ft. | 18359.6026 | 302933.4429
| b) First Floor | 2000 | 100 Sq.ft. | 18554.73 | 371094.6
| c) Second Floor | 65 | 100 Sq.ft. | 18683.51 | 12144.2815
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 25 | Each | 54.36 | 1359
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 15 | Each | 84.74 | 1271.1
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 5 | cwt | 7997.6 | 39988
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 50 | rft | 333.08 | 16654
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 6 | cwt | 6074.4 | 36446.4
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 45 | Sqft | 225.13 | 10130.85
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 85 | 100Rft | 2258.58 | 1919.793
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 850 | 100 Sq.ft | 135.06 | 1148.01
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 1150 | 100 Sq.ft | 284.54 | 3272.21
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 1500 | 100 Sq.ft | 2371.9061 | 35578.5908
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 550 | 100 Sft | 727.47 | 4001.085
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 800 | Sft | 71.69 | 57352
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 500 | 100 Sft. | 9097.3098 | 45486.5488
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 200 | 100 Sq.ft | 43.4293 | 86.8585
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 50 | 100 Sq.ft | 110.385 | 55.1925
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 2 | cwt | 5988.48 | 11976.96
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 20000 | 100 Sq.ft. | 139.9325 | 27986.5
30/125 | Plastering 1" (25 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 650 | 100 Sq.ft. | 2986.91 | 19414.915
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 350 | SQFT | 48.02 | 16807
| TOTAL OF SUB -HEAD A |  |  |  | 6429886.2415
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( MAIN HOSPITAL)
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 650 | 100 Sqft | 6102.5179 | 39666.3666
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 120 | 100 Rft. | 13968.6715 | 16762.4058
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 5600 | 100 Cft | 2823.86 | 158136.16
| TOTAL OF SUB HEAD B |  |  |  | 214564.9324
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( MAIN HOSPITAL)
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4. | 20 | Each | 3424.916 | 68498.32
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 20 | Each | 4601.3 | 92026
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4. | 25 | Each | 4628.14 | 115703.5
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 25 | Each | 863.83 | 21595.75
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 10 | Each | 12406.768 | 124067.68
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 85 | Each | 389.752 | 33128.92
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 10 | Each | 6611.132 | 66111.32
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 10 | Each | 968.44 | 9684.4
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 35 | Each | 279.75 | 9791.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 2 | Each | 66891 | 133782
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 250 | Rft | 68.32 | 17080
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 55 | Rft | 85.26 | 4689.3
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 45 | Rft | 120.35 | 5415.75
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 30 | Rft | 158.07 | 4742.1
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 155 | Rft | 35.21 | 5457.55
| Do. Do. 1 inch (25mm) dia. | 175 | Rft | 42.23 | 7390.25
| Do. Do. 1-1/4 inch (32 mm) dia.. | 225 | Rft | 64.23 | 14451.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 350 | Rft | 82.1 | 28735
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 250 | R.ft | 67.8153 | 16953.816
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 150 | R.ft | 88.2753 | 13241.2896
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 250 | R.ft | 127.734 | 31933.506
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 35 | Each | 882.9832 | 30904.412
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 10 | Each | 17442.4785 | 174424.7846
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m). | 3500 | %Cft | 599.7012 | 20989.5413
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe. | 350 | R.ft. | 250.26 | 87591
311/1 | Providing and fixing bath room accessories of set of 7 pieces consist of one cosmatic shelf, one towel rod with bracket, one soap dish, one tooth brush holder with glass and cover, one tissue paper holder one double hook one towel ring etc complete of approved quality as per direction of Engineer in-charge. | 0 | Each | 3986.62 | 0
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 35 | Each | 720.94 | 25232.9
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 17 | Each | 1500 | 25500
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 12 | Each | 105 | 1260
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 12 | Each | 125 | 1500
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 12 | Each | 215 | 2580
| PPRC Ball Valve 20 mm. | 12 | Each | 643.5 | 7722
| PPRC Ball Valve 25 mm. | 12 | Each | 783.75 | 9405
| TOTAL OF SUB HEAD C |  |  |  | 1263430.5675
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( MAIN HOSPITAL)
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 650 | Rft | 25 | 16250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 50 | 100 Sq.ft. | 12000 | 6000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 40 | Sft | 700 | 28000
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 1650 | Rft | 140 | 231000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 1650 | Rft | 225 | 371250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 80 | R.ft | 200.08 | 16006.4
| 8 inch dia | 30 | R.ft | 352.16 | 10564.8
| 12 inch dia | 30 | R.ft | 719.35 | 21580.5
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 30500 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 100 | Rft | 310 | 31000
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 4 | No | 350 | 1400
| Total of Non Schedule Items |  |  |  | 824551.7
SUMMARY
| Total of Sub Head 'A' | 6429886.2415
| Total of Sub Head 'B' | 214564.9324
| Total of Sub Head 'C' | 1263430.5675
| Total of Non-Schedule Items | 824551.7
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 8732433.4414

## valika Emergency
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KVSS HOSPITAL SITE KARACHI (Emergency ward & Radiology Department)
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 20 | Each | 197.795 | 3955.9
| b) First Floor |  | Each | 211.61 | 0
| c) Second Floor |  | Each | 225.42 | 0
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 20 | Each | 127.075 | 2541.5
| b) First Floor | 0 | Each | 137.58 | 0
| c) Second Floor | 0 | Each | 148.08 | 0
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 60 | 100 Cft. | 2773.55 | 1664.13
| b) First Floor | 0 | 100 Cft. | 3024.39 | 0
| c) Second Floor | 0 | 100 Cft. | 3253.68 | 0
| d) Third Floor | 0 | 100 Cft. | 3482.97 | 0
39/123 | Dismantling C.C. floor upto 2" (51 mm) thick in basement, plinth and ground floor including disposing off the material as directed within three chains (91.5 m). | 650 | 100 Cft. | 494.4875 | 3214.1687
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 650 | 100 Cft. | 988.975 | 6428.3375
| b) First Floor | 0 | 100 Cft. | 1239.82 | 0
| c) Second Floor | 0 | 100 Cft. | 1469.11 | 0
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 4000 | % Sq.ft. | 372.9375 | 14917.5
| b) First Floor | 0 | % Sq.ft. | 487.86 | 0
| c) Second Floor | 0 | % Sq.ft. | 602.78 | 0
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 650 | 100 Cft | 535.0885 | 3478.0752
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 110 | 100 Cft | 10085.8049 | 11094.3854
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 450 | 100 Cft. | 18172.93 | 81778.185
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 185 | 100 Cft. | 17514.88 | 32402.528
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 100 | 100 Cft. | 22448.44 | 22448.44
| b) First Floor | 0 | 100 Cft. | 23397.64 | 0
| c) Second Floor | 0 | 100 Cft. | 24149.14 | 0
| d) Third Floor | 0 | 100 Cft. | 24900.64 | 0
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 150 | 100 Cft. | 20668.6 | 31002.9
| b) First Floor | 0 | 100 Cft. | 21617.8 | 0
| c) Second Floor | 0 | 100 Cft. | 22369.25 | 0
| d) Third Floor | 0 | 100 Cft. | 23120.7 | 0
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 1350 | 100 Cft. | 20143.99 | 271943.865
| b) First Floor | 0 | 100 Cft. | 21093.19 | 0
| c) Second Floor | 0 | 100 Cft. | 21844.64 | 0
| d) Third Floor | 0 | 100 Cft. | 22596.09 | 0
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 80 | 100 Cft. | 22538.92 | 18031.136
| b) First Floor | 0 | 100 Cft. | 23488.12 | 0
| c) Second Floor | 0 | 100 Cft. | 24239.57 | 0
50/114 | Providing and laying reinforced cement concrete using 50 %screened graded bajri & 50 % crushed boulder 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2 ) at 28 days with a mix not leaner than 1:2:4 in straight stairs and landing of required section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 50 | 100 Cft. | 25545.28 | 12772.64
| b) First Floor | 0 | 100 Cft. | 26494.48 | 0
| c) Second Floor | 0 | 100 Cft. | 27245.93 | 0
| d) Third Floor | 0 | 100 Cft. | 27997.38 | 0
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 0 | 100 Cft. | 25857.43 | 0
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 850 | 100 Cft. | 15033.28 | 127782.88
| b) First Floor | 0 | 100 Cft. | 15857.05 | 0
| c) Second Floor | 0 | 100 Cft. | 16536.53 | 0
| d) Third Floor | 0 | 100 Cft. | 16536.53 | 0
2/122 | 1/4" (6.4 mm) thick cement plaster 1:4 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 2750 | %Sq.ft. | 1625.9797 | 44714.4426
| b) First Floor | 0 | % Sq.ft. | 1779.85 | 0
| c) Second Floor | 0 | % Sq.ft. | 1910.31 | 0
| d) Third Floor | 0 | % Sq.ft. | 2040.77 | 0
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 2500 | % Sq.ft. | 1730.7392 | 43268.4796
| b) First Floor | 0 | % Sq.ft. | 1884.61 | 0
| c) Second Floor | 0 | % Sq.ft. | 2015.07 | 0
| d) Third Floor | 0 | % Sq.ft. | 2145.53 | 0
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 1500 | % Sq.ft | 2204.0168 | 33060.2516
| b) First Floor | 0 | % Sq.ft | 2328.9 | 0
| c) Second Floor | 0 | % Sq.ft | 2406.95 | 0
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 1000 | % Sq.ft | 3075.7 | 30757
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 15 | Cft. | 4595.1353 | 68927.0294
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 375 | Sft. | 571.6761 | 214378.5317
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 25 | Sft. | 551.814 | 13795.3498
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 150 | Sq ft | 303.1167 | 45467.5104
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 0 | Sq ft | 503.6173 | 0
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 110 | Sq ft | 419.1321 | 46104.5357
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 250 | Sq ft | 91.9382 | 22984.5426
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 0 | Rft | 209.9983 | 0
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 400 | Rft | 35.6642 | 14265.671
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 0 | Sft | 327.3112 | 0
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 6650 | % Sq.ft | 124.434 | 8274.861
151/122 | Distempering with vinyle distemper (ICI) Dulux Paintex of approved make and shade in two coats over and including the cost of one priming coat of lime wash including sand papering, dusting, and filling the holes, cracks and inequalities, if any, at any height in any floor. | 3500 | % Sq.ft | 1053.5412 | 36873.942
162/122 | Painting with (ICI) Dulux plastic emulsion paint VIP of approved shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor . | 4500 | % Sq.ft | 2742.0796 | 123393.582
160/122 | Painting wood work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 250 | % Sq.ft | 2585.2182 | 6463.0455
159/122 | Painting iron work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 0 | % Sq.ft | 2776.6219 | 0
172/122 | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | 4000 | % Sq.ft | 1406.8847 | 56275.388
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 6500 | % Sq.ft | 560.9844 | 36463.9844
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 4000 | % Sq.ft | 505.095 | 20203.8
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 650 | % Sq.ft | 924.3325 | 6008.1613
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1650 | % Sq.ft | 955.7145 | 15769.2892
99/119 | Providing and fixing fully glazed Bronze anodized or powder coated aluminium Sliding windows as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators) deluxe model box section 95mm x 30mm and 1.6mm thick including the cost of aluminium netting ,fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 200 | Sq.ft. | 567.543 | 113508.6001
108/119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Hinged door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators), Economy model section, 76.2mm x 30mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 250 | Sq.ft. | 440.7402 | 110185.0612
120 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 450 | Sq.ft. | 106.1059 | 47747.6356
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 1000 | % Sq.ft | 3053.2494 | 30532.4942
157 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 1450 | 100 Rft. | 1368.1642 | 19838.3805
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 480 | Sq.ft. | 103.0965 | 49486.32
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 80 | Sqft | 363.11 | 29048.796
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 2 | Cwt | 9607.9425 | 19215.8849
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 0 | % Sq.ft | 12123.2262 | 0
| b) First Floor | 0 | % Sq.ft | 12365.19 | 0
| c) Second Floor | 0 | % Sq.ft | 12653.98 | 0
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 450 | % Sq.ft | 8408.2262 | 37837.0177
| b) First Floor | 0 | % Sq.ft | 8650.19 | 0
| c) Second Floor | 0 | % Sq.ft | 8938.98 | 0
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 160 | Cwt. | 6249.9391 | 999990.2495
| b) First Floor | 0 | Cwt. | 6323.42 | 0
| c) Second Floor | 0 | Cwt. | 6396.9 | 0
| d) Third Floor | 0 | Cwt. | 6470.38 | 0
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 0 | Rft | 157.1211 | 0
119/25 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor.. | 1200 | Sq.ft. | 494.9753 | 593970.3799
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 4 | Cwt. | 7634.0786 | 30536.3145
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 30 | Each | 2531.555 | 75946.65
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 20 | Each | 1063.8056 | 21276.112
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 0 | Each | 88.5392 | 0
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 0 | Each | 59.6369 | 0
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 0 | Each | 382.4221 | 0
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 0 | Rft. | 121.8152 | 0
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 6 | Each | 2420.5025 | 14523.015
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 8 | Each | 407.2754 | 3258.203
3 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 5000 | % Sq.ft. | 2659.7875 | 132989.3728
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 60 | Ib | 145.396 | 8723.76
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 8 | Rft. | 107.7375 | 861.9
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 220 | Rft. | 210.5485 | 46320.6792
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 20 | Each | 159.1642 | 3183.284
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 10 | Each | 629.85 | 6298.5
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 20 | Lbs. | 66.0667 | 1321.3344
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 0 | % Cft | 42.3057 | 0
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 0 | % Sq.ft. | 1878.9641 | 0
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 600 | Rft. | 9.6687 | 5801.25
63/117 | Providing and laying floor of 6mm (approx: 1/4") thick coloured glazed tiles 12" x 12" (304mm x 304mm) of master make (Pakistani) first grade in ground floor laid over 1" (25mm) thick cement mortar 1:2 (1 cement and 2 sand) including jointing and washing the tiles with white cement slurry a matching colour (by using pigment in white cement) and curing etc. complete. | 3000 | % Sq.ft. | 18359.6026 | 550788.0779
| b) First Floor | 0 | % Sq.ft. | 18554.73 | 0
| c) Second Floor | 0 | % Sq.ft. | 18683.51 | 0
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 25 | Each | 54.36 | 1359
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 15 | Each | 84.74 | 1271.1
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 0 | cwt | 7997.6 | 0
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 0 | rft | 333.08 | 0
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 12 | cft | 1832.57 | 21990.84
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 50 | Sqft | 678.32 | 33916
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 30 | Sq. In | 0.95 | 28.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 0 | cwt | 6074.4 | 0
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 45 | Sqft | 225.13 | 10130.85
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 85 | 100Rft | 2258.58 | 1919.793
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 1650 | 100Rft | 1392.7559 | 22980.4726
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 0 | % Sq.ft | 135.06 | 0
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 0 | % Sq.ft | 284.54 | 0
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 850 | % Sq.ft | 2371.9061 | 20161.2014
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 0 | 100 Sft | 727.47 | 0
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 1500 | Sft | 71.69 | 107535
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 1200 | 100 Sft. | 9097.3098 | 109167.717
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 0 | % Sq.ft | 43.4293 | 0
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 0 | 100 Sq.ft | 110.385 | 0
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 0 | cwt | 5988.48 | 0
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 10000 | % Sq.ft. | 139.9325 | 13993.25
30/125 | Plastering 1" (25 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 300 | % Sq.ft. | 2986.91 | 8960.73
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required. | 150 | SQFT | 48.02 | 7203
| TOTAL OF SUB -HEAD A |  |  |  | 4896083.0954
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KVSS HOSPITAL SITE KARACHI (Emergency ward & Radiology Department)
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 0 | % Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | % Sq.ft. | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 1500 | 100 Cft | 2823.86 | 42357.9
| TOTAL OF SUB HEAD B |  |  |  | 42357.9
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KVSS HOSPITAL SITE KARACHI (Emergency ward & Radiology Department)
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 10 | Each | 4601.3 | 46013
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4. | 10 | Each | 4628.14 | 46281.4
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal. | 10 | Each | 863.83 | 8638.3
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 2 | Each | 12406.768 | 24813.536
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 20 | Each | 389.752 | 7795.04
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 10 | Each | 6611.132 | 66111.32
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 8 | Each | 968.44 | 7747.52
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 8 | Each | 534.3008 | 4274.4064
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 8 | Each | 595.3024 | 4762.4192
10/302 | Providing and fixing bath room accessories of set of 7 pieces consist of one cosmatic shelf, one towel rod with bracket, one soap dish, one tooth brush holder with glass and cover, one tissue paper holder one double hook one towel ring etc complete of approved quality as per direction of Engineer in-charge. | 0 | Each | 3986.62 | 0
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 20 | Each | 279.75 | 5595
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 0 | Each | 66891 | 0
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 40 | Rft | 68.32 | 2732.8
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 0 | Rft | 85.26 | 0
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 20 | Rft | 120.35 | 2407
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 0 | Rft | 158.07 | 0
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 10 | Rft | 170.58 | 1705.8
| Do. 2inches (50 mm) dia pipe (ILLM). | 0 | Rft | 232.03 | 0
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 60 | Rft | 35.21 | 2112.6
| Do. Do. 1 inch (25mm) dia. | 50 | Rft | 42.23 | 2111.5
| Do. Do. 1-1/4 inch (32 mm) dia.. | 25 | Rft | 64.23 | 1605.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 30 | Rft | 82.1 | 2463
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 100 | R.ft | 67.8153 | 6781.5264
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 50 | R.ft | 88.2753 | 4413.7632
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 50 | R.ft | 127.734 | 6386.7012
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 10 | Each | 882.9832 | 8829.832
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 2 | Each | 17442.4785 | 34884.9569
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 3500 | %Cft | 599.7012 | 20989.5413
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe.. | 350 | R.ft. | 250.26 | 87591
311/1 | Providing and fixing bath room accessories of set of 7 pieces consist of one cosmatic shelf, one towel rod with bracket, one soap dish, one tooth brush holder with glass and cover, one tissue paper holder one double hook one towel ring etc complete of approved quality as per direction of Engineer in-charge. | 0 | Each | 3986.62 | 0
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 20 | Cft. | 664.8382 | 13296.764
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 10 | Each | 1500 | 15000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 5 | Each | 105 | 525
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 4 | Each | 215 | 860
| PPRC Ball Valve 20 mm. | 4 | Each | 643.5 | 2574
| PPRC Ball Valve 25 mm. | 4 | Each | 783.75 | 3135
| TOTAL OF SUB HEAD C |  |  |  | 496217.2366
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KVSS HOSPITAL SITE KARACHI (Emergency ward & Radiology Department)
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 0 | Each | 4500 | 0
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 250 | Rft | 25 | 6250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 450 | % Sq.ft. | 12000 | 54000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 0 | Sft | 700 | 0
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 150 | Rft | 140 | 21000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 150 | Rft | 225 | 33750
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 40 | R.ft | 200.08 | 8003.2
| 8 inch dia | 30 | R.ft | 352.16 | 10564.8
| 12 inch dia | 20 | R.ft | 719.35 | 14387
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 30500 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 100 | Rft | 550 | 55000
| b) 1/2 " dia | 50 | Rft | 310 | 15500
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 350 | 700
| Total Of Non Schedule Items |  |  |  | 219155
SUMMARY
| Total of Sub Head 'A' | 4896083.0954
| Total of Sub Head 'B' | 42357.9
| Total of Sub Head 'C' | 496217.2366
| Total of Non-Schedule Items | 219155
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 5653813.232

## valik doctor
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( DOCTOR'SRESIDENCE )
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 16 | Each | 197.795 | 3164.72
| b) First Floor | 15 | Each | 211.61 | 3174.15
| c) Second Floor | 22 | Each | 225.42 | 4959.24
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 20 | Each | 127.075 | 2541.5
| b) First Floor | 30 | Each | 137.58 | 4127.4
| c) Second Floor | 20 | Each | 148.08 | 2961.6
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 45 | Cft. | 4595.1353 | 206781.0881
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 450 | Sft. | 571.6761 | 257254.238
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 35 | 100 Cft. | 2773.55 | 970.7425
| b) First Floor | 100 | 100 Cft. | 3024.39 | 3024.39
| c) Second Floor | 250 | 100 Cft. | 3253.68 | 8134.2
| d) Third Floor | 2500 | 100 Cft. | 3482.97 | 87074.25
56/114+136+159+160 | Providing and laying reinforced cement concrete using crushed graded boulder 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2 ) at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in second floor | 2500 | 100 Cft. | 22538.46 | 563461.5
114/59+136 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch (15.52 N/mm2) at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 25 | 100 Cft. | 22538.92 | 5634.73
| b) First Floor | 50 | 100 Cft. | 23480.12 | 11740.06
| c) Second Floor | 450 | 100 Cft. | 24239.57 | 109078.065
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 2 | Cwt. | 6249.9391 | 12499.8781
| b) First Floor | 2 | Cwt. | 6323.42 | 12646.84
| c) Second Floor | 80 | Cwt. | 6396.9 | 511752
| d) Third Floor | 10 | Cwt. | 6470.38 | 64703.8
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 100 | 100 Cft. | 988.975 | 988.975
| b) First Floor | 200 | 100 Cft. | 1239.82 | 2479.64
| c) Second Floor | 200 | 100 Cft. | 1469.11 | 2938.22
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 50 | 100 Cft. | 15033.28 | 7516.64
| b) First Floor | 55 | 100 Cft. | 15857.05 | 8721.3775
| c) Second Floor | 50 | 100 Cft. | 16536.53 | 8268.265
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 500 | 100 Sq.ft | 2204.0168 | 11020.0839
| b) First Floor | 1400 | 100 Sq.ft | 2328.9 | 32604.6
| c) Second Floor | 2500 | 100 Sq.ft | 2406.95 | 60173.75
2/122 | 1/4" (6.4 mm) thick cement plaster 1:4 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 300 | 100 SFT | 1625.9797 | 4877.9392
| b) First Floor | 200 | 100 SFT | 1779.85 | 3559.7
| c) Second Floor | 6500 | 100 SFT | 1910.31 | 124170.15
3/122 | 1/2" (13 mm) thick cement plaster 1:3 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, corners, and curing etc., complete. | 250 | 100 SFT | 2083.5953 | 5208.9883
| b) First Floor | 200 | 100 SFT | 2237.47 | 4474.94
| c) Second Floor | 450 | 100 SFT | 2367.93 | 10655.685
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 50 | 100 Sq.ft | 2328.1361 | 1164.0681
| b) First Floor | 550 | 100 Sq.ft | 2453.02 | 13491.61
| c) Second Floor | 650 | 100 Sq.ft | 2531.07 | 16451.955
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 50 | 100 Sq.ft | 3075.7 | 1537.85
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 25000 | 100 Sq.ft. | 560.9844 | 140246.0938
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 20000 | 100 Sq.ft. | 505.095 | 101019
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 18500 | 100 Sq.ft | 789.1413 | 145991.1313
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 4500 | 100 Sq.ft. | 751.51 | 33817.95
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 560 | 100 Sft. | 415.4358 | 2326.4405
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor.. | 375 | Sft | 494.9753 | 185615.7437
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 0 | Sq.ft. | 330.2261 | 0
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 0 | Sft | 629.3167 | 0
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 0 | Sq.ft. | 447.0099 | 0
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 0 | Sq.ft. | 106.1059 | 0
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 650 | 100 Sq.ft. | 3053.2494 | 19846.1212
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 0 | 100 Sqft | 17882.3933 | 0
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 70 | 100 Rft. | 1368.1642 | 957.7149
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 1500 | 100 Sq.ft. | 924.3325 | 13864.9875
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 2500 | 100 Sq.ft. | 955.7145 | 23892.8625
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 1500 | Sq.ft. | 103.0965 | 154644.75
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 0 | Sqft | 363.11 | 0
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 0 | Cwt | 9607.9425 | 0
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 0 | 100 Sq.ft | 12123.2262 | 0
| b) First Floor | 0 | 100 Sq.ft | 12365.19 | 0
| c) Second Floor | 0 | 100 Sq.ft | 12653.98 | 0
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 1650 | 100 Sq.ft | 8408.2262 | 138735.7315
| b) First Floor | 1650 | 100 Sq.ft | 8650.19 | 142728.135
| c) Second Floor | 1650 | 100 Sq.ft | 8938.98 | 147493.17
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 8 | Cwt. | 7634.0786 | 61072.629
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 30 | Each | 2531.555 | 75946.65
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 25000 | 100 Sq.ft. | 602.78 | 150695
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 10 | Each | 1063.8056 | 10638.056
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 0 | Each | 2420.5025 | 0
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 0 | Each | 407.2754 | 0
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 25000 | 100 Sq.ft. | 2659.7875 | 664946.8642
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 750 | Ib | 145.396 | 109047
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 650 | Rft. | 210.5485 | 136856.5521
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 45 | Each | 159.1642 | 7162.389
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 28 | Each | 629.85 | 17635.8
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 0 | % Cft | 42.3057 | 0
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 0 | 100 Sq.ft. | 1878.9641 | 0
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 500 | Rft. | 9.6687 | 4834.375
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 2 | cwt | 7997.6 | 15995.2
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 0 | rft | 333.08 | 0
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 18 | cft | 1832.57 | 32986.26
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 0 | 100 Sq.ft | 135.06 | 0
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 250 | 100 Sq.ft | 284.54 | 711.35
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 1500 | 100 Sq.ft | 2371.9061 | 35578.5908
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 0 | 100 Sft | 727.47 | 0
228/125 | Easing doors, windows and ventilators in all floors. | 15 | Each | 43.1 | 646.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 0 | Sft | 71.69 | 0
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 250 | 100 Sft. | 9097.3098 | 22743.2744
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 0 | 100 Sq.ft | 43.4293 | 0
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 0 | 100 Sq.ft | 110.385 | 0
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 5 | cwt | 5988.48 | 29942.4
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 25000 | 100 Sq.ft. | 139.9325 | 34983.125
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 250 | SQFT | 48.02 | 12005
| TOTAL OF SUB -HEAD A |  |  |  | 5005160.2616
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( DOCTOR'SRESIDENCE )
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 150 | 100 Sq.ft. | 3840.8809 | 5761.3214
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 45 | 100 Sq ft | 12266.26 | 5519.817
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 650 | 100 Sqft | 6102.5179 | 39666.3666
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 245 | 100 Rft. | 13968.6715 | 34223.2451
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 2550 | 100 Cft | 2823.86 | 72008.43
| TOTAL OF SUB HEAD B |  |  |  | 157179.1801
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( DOCTOR'SRESIDENCE )
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4.. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4.. | 10 | Each | 4601.3 | 46013
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4.. | 10 | Each | 4628.14 | 46281.4
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 10 | Each | 863.83 | 8638.3
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 5 | Each | 12406.768 | 62033.84
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 45 | Each | 389.752 | 17538.84
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 15 | Each | 279.75 | 4196.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 2 | Each | 66891 | 133782
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 120 | Rft | 68.32 | 8198.4
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 45 | Rft | 85.26 | 3836.7
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 30 | Rft | 120.35 | 3610.5
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 20 | Rft | 158.07 | 3161.4
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 125 | Rft | 35.21 | 4401.25
| Do. Do. 1 inch (25mm) dia. | 135 | Rft | 42.23 | 5701.05
| Do. Do. 1-1/4 inch (32 mm) dia.. | 125 | Rft | 64.23 | 8028.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 250 | Rft | 82.1 | 20525
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 250 | R.ft | 67.8153 | 16953.816
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 45 | R.ft | 88.2753 | 3972.3869
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 55 | R.ft | 127.734 | 7025.3713
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 20 | Each | 882.9832 | 17659.664
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 5 | Each | 17442.4785 | 87212.3923
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe.. | 350 | R.ft. | 250.26 | 87591
311/1 | Providing and fixing bath room accessories of set of 7 pieces consist of one cosmatic shelf, one towel rod with bracket, one soap dish, one tooth brush holder with glass and cover, one tissue paper holder one double hook one towel ring etc complete of approved quality as per direction of Engineer in-charge. | 0 | Each | 3986.62 | 0
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 35 | Each | 720.94 | 25232.9
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 8 | Each | 1500 | 12000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 6 | Each | 105 | 630
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 5 | Each | 215 | 1075
| PPRC Ball Valve 20 mm. | 5 | Each | 643.5 | 3217.5
| PPRC Ball Valve 25 mm. | 4 | Each | 783.75 | 3135
| TOTAL OF SUB HEAD C |  |  |  | 769563.565
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( DOCTOR'SRESIDENCE )
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 1200 | Rft | 25 | 30000
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 0 | 100 Sq.ft. | 12000 | 0
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 0 | Sft | 700 | 0
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 2150 | Rft | 140 | 301000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 1950 | Rft | 225 | 438750
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 110 | R.ft | 200.08 | 22008.8
| 8 inch dia | 150 | R.ft | 352.16 | 52824
| 12 inch dia | 50 | R.ft | 719.35 | 35967.5
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 1200 | Sft | 10 | 12000
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 5 | No | 4500 | 22500
| Bb) Carbon dioxide 5 Kg | 5 | No. | 5000 | 25000
| c) Foam 9 litre | 3 | No. | 8000 | 24000
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 2 | No. | 33250 | 66500
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 100 | Rft | 310 | 31000
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total of Non Schedule Items |  |  |  | 1158050.3
SUMMARY
| Total of Sub Head 'A' | 5005160.2616
| Total of Sub Head 'B' | 157179.1801
| Total of Sub Head 'C' | 769563.565
| Total of Non-Schedule Items | 1158050.3
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 7089953.3067

## valika para med
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( PARA MEDICAL RESIDENCE )
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 16 | Each | 197.795 | 3164.72
| b) First Floor | 25 | Each | 211.61 | 5290.25
| c) Second Floor | 30 | Each | 225.42 | 6762.6
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 20 | Each | 127.075 | 2541.5
| b) First Floor | 30 | Each | 137.58 | 4127.4
| c) Second Floor | 30 | Each | 148.08 | 4442.4
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 55 | Cft. | 4595.1353 | 252732.441
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 855 | Sft. | 571.6761 | 488783.0523
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 35 | 100 Cft. | 2773.55 | 970.7425
| b) First Floor | 100 | 100 Cft. | 3024.39 | 3024.39
| c) Second Floor | 350 | 100 Cft. | 3253.68 | 11387.88
| d) Third Floor | 3000 | 100 Cft. | 3482.97 | 104489.1
56/114+136+159+160 | Providing and laying reinforced cement concrete using crushed graded boulder 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2 ) at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in second floor | 3000 | 100 Cft. | 22538.46 | 676153.8
114/59+136 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch (15.52 N/mm2) at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 25 | 100 Cft. | 22538.92 | 5634.73
| b) First Floor | 50 | 100 Cft. | 23480.12 | 11740.06
| c) Second Floor | 450 | 100 Cft. | 24239.57 | 109078.065
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 2 | Cwt. | 6249.9391 | 12499.8781
| b) First Floor | 2 | Cwt. | 6323.42 | 12646.84
| c) Second Floor | 120 | Cwt. | 6396.9 | 767628
| d) Third Floor | 10 | Cwt. | 6470.38 | 64703.8
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 100 | 100 Cft. | 988.975 | 988.975
| b) First Floor | 200 | 100 Cft. | 1239.82 | 2479.64
| c) Second Floor | 200 | 100 Cft. | 1469.11 | 2938.22
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 50 | 100 Cft. | 15033.28 | 7516.64
| b) First Floor | 55 | 100 Cft. | 15857.05 | 8721.3775
| c) Second Floor | 50 | 100 Cft. | 16536.53 | 8268.265
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 500 | 100 Sq.ft | 2204.0168 | 11020.0839
| b) First Floor | 1400 | 100 Sq.ft | 2328.9 | 32604.6
| c) Second Floor | 2500 | 100 Sq.ft | 2406.95 | 60173.75
2/122 | 1/4" (6.4 mm) thick cement plaster 1:4 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 300 | 100 SFT | 1625.9797 | 4877.9392
| b) First Floor | 200 | 100 SFT | 1779.85 | 3559.7
| c) Second Floor | 6500 | 100 SFT | 1910.31 | 124170.15
3/122 | 1/2" (13 mm) thick cement plaster 1:3 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, corners, and curing etc., complete. | 150 | 100 SFT | 2083.5953 | 3125.393
| b) First Floor | 200 | 100 SFT | 2237.47 | 4474.94
| c) Second Floor | 450 | 100 SFT | 2367.93 | 10655.685
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 50 | 100 Sq.ft | 2328.1361 | 1164.0681
| b) First Floor | 250 | 100 Sq.ft | 2453.02 | 6132.55
| c) Second Floor | 650 | 100 Sq.ft | 2531.07 | 16451.955
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 50 | 100 Sq.ft | 3075.7 | 1537.85
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 0 | 100 Sq.ft. | 560.9844 | 0
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 30000 | 100 Sq.ft. | 124.434 | 37330.2
148/125 | Colour washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor.. | 35000 | 100 Sq.ft | 131.57 | 46049.5
159/125 | Snow ceming/duracem one renewal coat to walls and ceiling etc. including cleaning the old surface in any floor. | 30000 | 100 Sq.ft. | 677.4425 | 203232.75
155/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 560 | 100 Sft. | 415.4358 | 2326.4405
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor.. | 375 | Sft | 494.9753 | 185615.7437
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 0 | Sq.ft. | 330.2261 | 0
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 0 | Sft | 629.3167 | 0
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 0 | Sq.ft. | 447.0099 | 0
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 0 | Sq.ft. | 106.1059 | 0
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 650 | 100 Sq.ft. | 3053.2494 | 19846.1212
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 0 | 100 Sqft | 17882.3933 | 0
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 70 | 100 Rft. | 1368.1642 | 957.7149
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 1500 | 100 Sq.ft. | 924.3325 | 13864.9875
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 2500 | 100 Sq.ft. | 955.7145 | 23892.8625
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 1500 | Sq.ft. | 103.0965 | 154644.75
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 0 | Sqft | 363.11 | 0
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 0 | Cwt | 9607.9425 | 0
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 0 | 100 Sq.ft | 12123.2262 | 0
| b) First Floor | 0 | 100 Sq.ft | 12365.19 | 0
| c) Second Floor | 0 | 100 Sq.ft | 12653.98 | 0
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 1650 | 100 Sq.ft | 8408.2262 | 138735.7315
| b) First Floor | 1650 | 100 Sq.ft | 8650.19 | 142728.135
| c) Second Floor | 1650 | 100 Sq.ft | 8938.98 | 147493.17
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 8 | Cwt. | 7634.0786 | 61072.629
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 30 | Each | 2531.555 | 75946.65
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 25000 | 100 Sq.ft. | 602.78 | 150695
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 10 | Each | 1063.8056 | 10638.056
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 0 | Each | 2420.5025 | 0
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 0 | Each | 407.2754 | 0
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 25000 | 100 Sq.ft. | 2659.7875 | 664946.8642
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 750 | Ib | 145.396 | 109047
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 650 | Rft. | 210.5485 | 136856.5521
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 45 | Each | 159.1642 | 7162.389
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 28 | Each | 629.85 | 17635.8
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 0 | % Cft | 42.3057 | 0
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 0 | 100 Sq.ft. | 1878.9641 | 0
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 2000 | Rft. | 9.6687 | 19337.5
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 0 | cwt | 7997.6 | 0
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 0 | rft | 333.08 | 0
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 18 | cft | 1832.57 | 32986.26
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 0 | Sqft | 678.32 | 0
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 50 | Sq. In | 0.95 | 47.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 0 | Sqft | 225.13 | 0
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 5000 | 100Rft | 1392.7559 | 69637.7958
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 0 | 100 Sq.ft | 135.06 | 0
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 0 | 100 Sq.ft | 284.54 | 0
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 5000 | 100 Sq.ft | 2371.9061 | 118595.3025
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 0 | Sft | 96.8 | 0
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 0 | 100 Sft | 727.47 | 0
228/125 | Easing doors, windows and ventilators in all floors. | 15 | Each | 43.1 | 646.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 750 | Sft | 8.84 | 6630
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 0 | Sft | 71.69 | 0
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 0 | 100 Sft. | 9097.3098 | 0
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 0 | 100 Sq.ft | 43.4293 | 0
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 0 | 100 Sq.ft | 110.385 | 0
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 0 | cwt | 5988.48 | 0
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 0 | 100 Sq.ft. | 139.9325 | 0
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 0 | SQFT | 48.02 | 0
| TOTAL OF SUB -HEAD A |  |  |  | 5491246.8818
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( PARA MEDICAL RESIDENCE )
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 150 | 100 Sq.ft. | 3840.8809 | 5761.3214
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 45 | 100 Sq ft | 12266.26 | 5519.817
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 650 | 100 Sqft | 6102.5179 | 39666.3666
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 245 | 100 Rft. | 13968.6715 | 34223.2451
5/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 2550 | 100 Cft | 2823.86 | 72008.43
| TOTAL OF SUB HEAD B |  |  |  | 157179.1801
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( PARA MEDICAL RESIDENCE )
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4.. | 15 | Each | 3424.916 | 51373.74
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4.. | 10 | Each | 4601.3 | 46013
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4.. | 10 | Each | 4628.14 | 46281.4
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 10 | Each | 863.83 | 8638.3
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 0 | Each | 12406.768 | 0
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 45 | Each | 389.752 | 17538.84
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 15 | Each | 279.75 | 4196.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 2 | Each | 66891 | 133782
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 120 | Rft | 68.32 | 8198.4
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 45 | Rft | 85.26 | 3836.7
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 30 | Rft | 120.35 | 3610.5
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 20 | Rft | 158.07 | 3161.4
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 125 | Rft | 35.21 | 4401.25
| Do. Do. 1 inch (25mm) dia. | 135 | Rft | 42.23 | 5701.05
| Do. Do. 1-1/4 inch (32 mm) dia.. | 125 | Rft | 64.23 | 8028.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 250 | Rft | 82.1 | 20525
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 250 | R.ft | 67.8153 | 16953.816
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 45 | R.ft | 88.2753 | 3972.3869
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 55 | R.ft | 127.734 | 7025.3713
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 20 | Each | 882.9832 | 17659.664
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 8 | Each | 17442.4785 | 139539.8277
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe.. | 350 | R.ft. | 250.26 | 87591
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 8 | Each | 1500 | 12000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 6 | Each | 105 | 630
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 5 | Each | 215 | 1075
| PPRC Ball Valve 20 mm. | 5 | Each | 643.5 | 3217.5
| PPRC Ball Valve 25 mm. | 4 | Each | 783.75 | 3135
| TOTAL OF SUB HEAD C |  |  |  | 739697.2404
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI ( PARA MEDICAL RESIDENCE )
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 1200 | Rft | 25 | 30000
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 0 | 100 Sq.ft. | 12000 | 0
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 0 | Sft | 700 | 0
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 2150 | Rft | 140 | 301000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 1950 | Rft | 225 | 438750
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 110 | R.ft | 200.08 | 22008.8
| 8 inch dia | 150 | R.ft | 352.16 | 52824
| 12 inch dia | 50 | R.ft | 719.35 | 35967.5
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 1200 | Sft | 10 | 12000
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 5 | No | 4500 | 22500
| Bb) Carbon dioxide 5 Kg | 5 | No. | 5000 | 25000
| c) Foam 9 litre | 3 | No. | 8000 | 24000
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 2 | No. | 33250 | 66500
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 100 | Rft | 310 | 31000
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total of Non Schedule Items |  |  |  | 1158050.3
SUMMARY
| Total of Sub Head 'A' | 5491246.8818
| Total of Sub Head 'B' | 157179.1801
| Total of Sub Head 'C' | 739697.2404
| Total of Non-Schedule Items | 1158050.3
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 7546173.6023

## Hyd
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF GANJU TAKAR SITE HYDERABAD
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 6 | Each | 197.795 | 1186.77
| b) First Floor | 12 | Each | 211.61 | 2539.32
| c) Second Floor | 1 | Each | 225.42 | 225.42
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 6 | Each | 127.075 | 762.45
| b) First Floor | 12 | Each | 137.58 | 1650.96
| c) Second Floor | 1 | Each | 148.08 | 148.08
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 30 | Cft. | 4595.1353 | 137854.0587
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 20 | 100 Cft. | 2773.55 | 554.71
| b) First Floor | 50 | 100 Cft. | 3024.39 | 1512.195
| c) Second Floor | 25 | 100 Cft. | 3253.68 | 813.42
| d) Third Floor | 0 | 100 Cft. | 3482.97 | 0
9/123 | Dismantling burnt brick masonry in lime or cement mortar foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed within three chains (91.5 m).. | 450 | 100 Cft. | 988.975 | 4450.3875
| b) First Floor | 650 | 100 Cft. | 1103.9 | 7175.35
| c) Second Floor | 150 | 100 Cft. | 1385.51 | 2078.265
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 0 | 100 Cft. | 988.975 | 0
| b) First Floor | 0 | 100 Cft. | 1239.82 | 0
| c) Second Floor | 0 | 100 Cft. | 1469.11 | 0
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 650 | 100 Cft | 535.0885 | 3478.0752
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 110 | 100 Cft | 10085.8049 | 11094.3854
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 450 | 100 Cft. | 18172.93 | 81778.185
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 185 | 100 Cft. | 17514.88 | 32402.528
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 210 | 100 Cft. | 22448.44 | 47141.724
| b) First Floor | 175 | 100 Cft. | 23397.64 | 40945.87
| c) Second Floor | 55 | 100 Cft. | 24149.14 | 13282.027
| d) Third Floor | 0 | 100 Cft. | 24900.64 | 0
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 350 | 100 Cft. | 20668.6 | 72340.1
| b) First Floor | 285 | 100 Cft. | 21617.8 | 61610.73
| c) Second Floor | 355 | 100 Cft. | 22369.25 | 79410.8375
| d) Third Floor | 0 | 100 Cft. | 23120.7 | 0
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 350 | 100 Cft. | 20143.99 | 70503.965
| b) First Floor | 255 | 100 Cft. | 21093.19 | 53787.6345
| c) Second Floor | 120 | 100 Cft. | 21844.64 | 26213.568
| d) Third Floor | 0 | 100 Cft. | 22596.09 | 0
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 35 | 100 Cft. | 22538.92 | 7888.622
| b) First Floor | 45 | 100 Cft. | 23488.12 | 10569.654
| c) Second Floor | 30 | 100 Cft. | 24239.57 | 7271.871
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 20 | 100 Cft. | 25857.43 | 5171.486
24/112 | Providing and laying first class solid burnt brick masonry set in cement mortar 1:6 in straight or curved walls 9 to 13-1/2 inches (229 mm to 343 mm) thick including scaffolding, raking, out joints and curing etc. complete in ground floor superstructure . | 650 | 100 Cft. | 21905.3463 | 142384.7508
| b) First Floor | 950 | 100 Cft. | 22096.78 | 209919.41
| c) Second Floor | 25 | 100 Cft. | 22776.26 | 5694.065
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 1500 | 100 Cft. | 1730.7392 | 25961.0877
| b) First Floor | 2500 | 100 Cft. | 1935.9 | 48397.5
| c) Second Floor | 75 | 100 Cft. | 2066.36 | 1549.77
56/114+136+159+160 | Providing and laying reinforced cement concrete using crushed graded boulder 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2 ) at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in second floor | 250 | 100 Cft. | 22538.46 | 56346.15
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 60 | Cwt. | 6249.9391 | 374996.3436
| b) First Floor | 20 | Cwt. | 6323.42 | 126468.4
| c) Second Floor | 15 | Cwt. | 6396.9 | 95953.5
| d) Third Floor | 0 | Cwt. | 6470.38 | 0
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 0 | 100 Cft. | 15033.28 | 0
| b) First Floor | 0 | 100 Cft. | 15857.05 | 0
| c) Second Floor | 0 | 100 Cft. | 16536.53 | 0
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 350 | 100 Sq.ft | 2204.0168 | 7714.0587
| b) First Floor | 450 | 100 Sq.ft | 2328.9 | 10480.05
| c) Second Floor | 1600 | 100 Sq.ft | 2406.95 | 38511.2
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 150 | 100 Sq.ft | 2328.1361 | 3492.2042
| b) First Floor | 560 | 100 Sq.ft | 2453.02 | 13736.912
| c) Second Floor | 250 | 100 Sq.ft | 2531.07 | 6327.675
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 250 | 100 Sq.ft | 3075.7 | 7689.25
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 15500 | 100 Sq.ft. | 560.9844 | 86952.5781
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 250 | Sft. | 571.6761 | 142919.0211
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 25 | Sft. | 551.814 | 13795.3498
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 150 | Sq ft | 303.1167 | 45467.5104
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 65 | Sq ft | 503.6173 | 32735.1229
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 220 | Sq ft | 419.1321 | 92209.0715
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 675 | Sq ft | 91.9382 | 62058.2651
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 125 | Sft | 327.3112 | 40913.9046
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 1250 | 100 Sq.ft. | 505.095 | 6313.6875
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 2650 | 100 Sq.ft | 789.1413 | 20912.2431
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 4850 | 100 Sq.ft. | 751.51 | 36448.235
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 160 | 100 Sft. | 415.4358 | 664.6973
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor.. | 85 | Sft | 494.9753 | 42072.9019
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 250 | Sq.ft. | 330.2261 | 82556.52
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 250 | Sft | 629.3167 | 157329.1748
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 250 | Sq.ft. | 447.0099 | 111752.4859
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 550 | Sq.ft. | 106.1059 | 58358.2213
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 1520 | 100 Sq.ft. | 3053.2494 | 46409.3912
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 3500 | 100 Sqft | 17882.3933 | 625883.764
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 5000 | Sft | 74.8883 | 374441.53
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 1200 | 100 Rft. | 1368.1642 | 16417.9701
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 1500 | 100 Sq.ft. | 924.3325 | 13864.9875
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 2500 | 100 Sq.ft. | 955.7145 | 23892.8625
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 6500 | 100 Sq.ft. | 124.434 | 8088.21
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 1250 | Sq.ft. | 103.0965 | 128870.625
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 125 | Sqft | 363.11 | 45388.7438
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 15 | Cwt | 9607.9425 | 144119.1368
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 50 | 100 Sq.ft | 12123.2262 | 6061.6131
| b) First Floor | 25 | 100 Sq.ft | 12365.19 | 3091.2975
| c) Second Floor | 25 | 100 Sq.ft | 12653.98 | 3163.495
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 1650 | 100 Sq.ft | 8408.2262 | 138735.7315
| b) First Floor | 1850 | 100 Sq.ft | 8650.19 | 160028.515
| c) Second Floor | 85 | 100 Sq.ft | 8938.98 | 7598.133
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 8 | Cwt. | 7634.0786 | 61072.629
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 10 | Each | 2531.555 | 25315.55
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 5000 | 100 Sq.ft. | 602.78 | 30139
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 25 | Each | 1063.8056 | 26595.14
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 5 | Each | 2420.5025 | 12102.5125
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 3 | Each | 407.2754 | 1221.8261
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 5000 | 100 Sq.ft. | 2659.7875 | 132989.3728
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 450 | Ib | 145.396 | 65428.2
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 650 | Rft. | 210.5485 | 136856.5521
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 45 | Each | 159.1642 | 7162.389
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 28 | Each | 629.85 | 17635.8
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 250 | % Cft | 42.3057 | 105.7643
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 560 | 100 Sq.ft. | 1878.9641 | 10522.199
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 500 | Rft. | 9.6687 | 4834.375
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 2 | cwt | 7997.6 | 15995.2
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 25 | rft | 333.08 | 8327
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 850 | 100 Sq.ft | 135.06 | 1148.01
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 250 | 100 Sq.ft | 284.54 | 711.35
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 1500 | 100 Sq.ft | 2371.9061 | 35578.5908
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 450 | 100 Sft | 727.47 | 3273.615
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 1250 | Sft | 71.69 | 89612.5
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 30 | lbs | 180.48 | 5414.4
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 250 | 100 Sft. | 9097.3098 | 22743.2744
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 50 | 100 Sq.ft | 43.4293 | 21.7146
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 1500 | 100 Sq.ft | 110.385 | 1655.775
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 15 | cwt | 5988.48 | 89827.2
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 25000 | 100 Sq.ft. | 139.9325 | 34983.125
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 250 | SQFT | 48.02 | 12005
| TOTAL OF SUB -HEAD A |  |  |  | 5767582.627
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF GANJU TAKAR SITE HYDERABAD
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 2500 | 100 Sq.ft. | 3840.8809 | 96022.0234
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 245 | 100 Sq ft | 12266.26 | 30052.3369
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 650 | 100 Sqft | 6102.5179 | 39666.3666
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 245 | 100 Rft. | 13968.6715 | 34223.2451
5/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 2500 | 100 Cft | 2823.86 | 70596.5
| TOTAL OF SUB HEAD B |  |  |  | 270560.4721
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF GANJU TAKAR SITE HYDERABAD
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4.. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4.. | 10 | Each | 4601.3 | 46013
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4.. | 10 | Each | 4628.14 | 46281.4
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 10 | Each | 863.83 | 8638.3
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 5 | Each | 12406.768 | 62033.84
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 20 | Each | 389.752 | 7795.04
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 15 | Each | 279.75 | 4196.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 120 | Rft | 68.32 | 8198.4
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 45 | Rft | 85.26 | 3836.7
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 30 | Rft | 120.35 | 3610.5
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 20 | Rft | 158.07 | 3161.4
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 125 | Rft | 35.21 | 4401.25
| Do. Do. 1 inch (25mm) dia. | 135 | Rft | 42.23 | 5701.05
| Do. Do. 1-1/4 inch (32 mm) dia.. | 125 | Rft | 64.23 | 8028.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 250 | Rft | 82.1 | 20525
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 250 | R.ft | 67.8153 | 16953.816
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 45 | R.ft | 88.2753 | 3972.3869
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 55 | R.ft | 127.734 | 7025.3713
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 20 | Each | 882.9832 | 17659.664
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 5 | Each | 17442.4785 | 87212.3923
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe.. | 150 | R.ft. | 250.26 | 37539
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 8 | Each | 1500 | 12000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 6 | Each | 105 | 630
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 5 | Each | 215 | 1075
| PPRC Ball Valve 20 mm. | 5 | Each | 643.5 | 3217.5
| PPRC Ball Valve 25 mm. | 4 | Each | 783.75 | 3135
| TOTAL OF SUB HEAD C |  |  |  | 624853.265
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF GANJU TAKAR SITE HYDERABAD
Non- Schedule Item based on Prevailing Market Rates
1 | Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
2 | Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 550 | Rft | 25 | 13750
3 | Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 1250 | 100 Sq.ft. | 12000 | 150000
4 | Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 50 | Sft | 700 | 35000
5 | Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 675 | Rft | 140 | 94500
6 | Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 450 | Rft | 225 | 101250
7 | Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 75 | R.ft | 200.08 | 15006
| 8 inch dia | 50 | R.ft | 352.16 | 17608
| 12 inch dia | 50 | R.ft | 719.35 | 35967.5
8 | Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
9 | Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 33250 | 0
GAS WORK
10 | Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 75 | Rft | 310 | 23250
11 | Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
12 | Providing & installing Fibre Glass Roof over MS profile section frame with prime coat and two coat anti rust enemal paint and 2. 5 mm thick two layered insulated fibre glass top sheet with side vantilation shaft as per Drawing & design at existing void complete as per specification. | 685 | sft | 550 | 376750
| Total Of Non Schedule Items |  |  |  | 959581.5
SUMMARY
| Total of Sub Head 'A' | 5767582.627
| Total of Sub Head 'B' | 270560.4721
| Total of Sub Head 'C' | 624853.265
| Total of Non-Schedule Items | 959581.5
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 7622577.8641

## Lines Area Eye Clinic
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (FIRST FLOOR EYE CLINIC )
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 8 | Each | 197.795 | 1582.36
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 8 | Each | 127.075 | 1016.6
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 5 | 100 Cft. | 2773.55 | 138.6775
39/123 | Dismantling C.C. floor upto 2" (51 mm) thick in basement, plinth and ground floor including disposing off the material as directed within three chains (91.5 m). | 25 | 100 Cft. | 494.4875 | 123.6219
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 650 | 100 Cft. | 988.975 | 6428.3375
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 25 | 100 Sq.ft. | 372.9375 | 93.2344
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 0 | 100 Cft | 535.0885 | 0
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 10 | 100 Cft | 10085.8049 | 1008.5805
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 10 | 100 Cft. | 18172.93 | 1817.293
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 10 | 100 Cft. | 17514.88 | 1751.488
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 10 | 100 Cft. | 22448.44 | 2244.844
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 20 | 100 Cft. | 20668.6 | 4133.72
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 250 | 100 Cft. | 20143.99 | 50359.975
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 60 | 100 Cft. | 22538.92 | 13523.352
50/114 | Providing and laying reinforced cement concrete using 50 %screened graded bajri & 50 % crushed boulder 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2 ) at 28 days with a mix not leaner than 1:2:4 in straight stairs and landing of required section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 20 | 100 Cft. | 25545.28 | 5109.056
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 20 | 100 Cft. | 25857.43 | 5171.486
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 860 | 100 Cft. | 15033.28 | 129286.208
2/122 | 1/4" (6.4 mm) thick cement plaster 1:4 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 250 | 100 Sq.ft. | 1625.9797 | 4064.9493
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 1800 | 100 Sq.ft. | 1730.7392 | 31153.3053
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 20 | 100 Sq.ft | 2204.0168 | 440.8034
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 120 | 100 Sq.ft | 3075.7 | 3690.84
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 15 | Cft. | 4595.1353 | 68927.0294
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 120 | Sft. | 571.6761 | 68601.1301
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required. | 20 | Sft. | 551.814 | 11036.2799
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required. | 20 | Sq ft | 303.1167 | 6062.3347
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required. | 25 | Sq ft | 503.6173 | 12590.4319
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required. | 25 | Sq ft | 419.1321 | 10478.3036
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 250 | Sq ft | 91.9382 | 22984.5426
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 125 | Sft | 327.3112 | 40913.9046
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 0 | 100 Sq.ft | 124.434 | 0
162/122 | Painting with (ICI) Dulux plastic emulsion paint VIP of approved shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor . | 0 | 100 Sq.ft | 2742.0796 | 0
160/122 | Painting wood work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 650 | 100 Sq.ft | 2585.2182 | 16803.9184
159/122 | Painting iron work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor. | 150 | 100 Sq.ft | 2776.6219 | 4164.9329
172/122 | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | 0 | 100 Sq.ft | 1406.8847 | 0
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 5000 | 100 Sq.ft. | 560.9844 | 28049.2188
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 16500 | 100 Sq.ft. | 505.095 | 83340.675
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 250 | 100 Sq.ft. | 924.3325 | 2310.8313
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 120 | 100 Sq.ft. | 955.7145 | 1146.8574
99/119 | Providing and fixing fully glazed Bronze anodized or powder coated aluminium Sliding windows as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators) deluxe model box section 95mm x 30mm and 1.6mm thick including the cost of aluminium netting ,fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 567.543 | 34052.58
108/119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Hinged door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators), Economy model section, 76.2mm x 30mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 80 | Sq.ft. | 440.7402 | 35259.2196
120 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 260 | Sq.ft. | 106.1059 | 27587.5228
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 650 | 100 Sq.ft. | 3053.2494 | 19846.1212
157 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 450 | 100 Rft. | 1368.1642 | 6156.7388
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 650 | Sq.ft. | 103.0965 | 67012.725
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor. | 80 | Sqft | 363.11 | 29048.796
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 0 | Cwt | 9607.9425 | 0
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 60 | 100 Sq.ft | 12123.2262 | 7273.9357
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 80 | 100 Sq.ft | 8408.2262 | 6726.5809
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 0 | Cwt. | 6249.9391 | 0
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 15 | Rft | 157.1211 | 2356.816
119/25 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | 20 | Sq.ft. | 494.9753 | 9899.5063
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 2 | Cwt. | 7634.0786 | 15268.1573
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 10 | Each | 2531.555 | 25315.55
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 5 | Each | 1063.8056 | 5319.028
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 10 | Each | 59.6369 | 596.3685
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm. | 10 | Each | 382.4221 | 3824.2208
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 10 | Rft. | 121.8152 | 1218.152
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge. | 2 | Each | 2420.5025 | 4841.005
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size. | 4 | Each | 407.2754 | 1629.1015
3 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent. | 60 | 100 Sq.ft. | 2659.7875 | 1595.8725
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 6 | Ib | 145.396 | 872.376
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 10 | Rft. | 107.7375 | 1077.375
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 120 | Rft. | 210.5485 | 25265.825
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 10 | Each | 159.1642 | 1591.642
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 5 | Each | 629.85 | 3149.25
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 2 | Lbs. | 66.0667 | 132.1334
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 0 | % Cft | 42.3057 | 0
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 50 | 100 Sq.ft. | 1878.9641 | 939.482
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 200 | Rft. | 9.6687 | 1933.75
63/117 | Providing and laying floor of 6mm (approx: 1/4") thick coloured glazed tiles 12" x 12" (304mm x 304mm) of master make (Pakistani) first grade in ground floor laid over 1" (25mm) thick cement mortar 1:2 (1 cement and 2 sand) including jointing and washing the tiles with white cement slurry a matching colour (by using pigment in white cement) and curing etc. complete. | 5500 | 100 Sq.ft. | 18359.6026 | 1009778.1429
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 5 | Each | 54.36 | 271.8
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 2 | Each | 84.74 | 169.48
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 5 | lbs | 76.49 | 382.45
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 0 | cwt | 7997.6 | 0
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors. | 0 | rft | 333.08 | 0
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height. | 560 | Sq. In | 0.95 | 532
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete. | 0 | cwt | 6074.4 | 0
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 45 | Sqft | 225.13 | 10130.85
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 20 | 100Rft | 2258.58 | 451.716
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 25 | 100Rft | 1392.7559 | 348.189
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 50 | 100 Sq.ft | 135.06 | 67.53
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 0 | 100 Sq.ft | 284.54 | 0
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 60 | 100 Sq.ft | 2371.9061 | 1423.1436
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 60 | Sft | 96.8 | 5808
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor. | 0 | 100 Sft | 727.47 | 0
228/125 | Easing doors, windows and ventilators in all floors. | 20 | Each | 43.1 | 862
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 2000 | Sft | 71.69 | 143380
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 650 | 100 Sft. | 9097.3098 | 59132.5134
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete. | 0 | cwt | 5988.48 | 0
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 6500 | 100 Sq.ft. | 139.9325 | 9095.6125
30/125 | Plastering 1" (25 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 50 | 100 Sq.ft. | 2986.91 | 1493.455
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required. | 350 | SQFT | 48.02 | 16807
| TOTAL OF SUB -HEAD A |  |  |  | 2336579.1328
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (FIRST FLOOR EYE CLINIC )
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired. | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
5/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 4800 | 100 Cft | 2823.86 | 135545.28
| TOTAL OF SUB HEAD B |  |  |  | 135545.28
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (FIRST FLOOR EYE CLINIC )
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 10 | Each | 4601.3 | 46013
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4. | 10 | Each | 4628.14 | 46281.4
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal. | 10 | Each | 863.83 | 8638.3
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 10 | Each | 389.752 | 3897.52
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 10 | Each | 6611.132 | 66111.32
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 5 | Each | 534.3008 | 2671.504
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 5 | Each | 720.94 | 3604.7
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 10 | Each | 279.75 | 2797.5
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 40 | Rft | 68.32 | 2732.8
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 10 | Rft | 85.26 | 852.6
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 24 | Rft | 120.35 | 2888.4
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 12 | Rft | 158.07 | 1896.84
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 15 | Rft | 170.58 | 2558.7
| Do. 2inches (50 mm) dia pipe (ILLM). | 10 | Rft | 232.03 | 2320.3
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 25 | Rft | 35.21 | 880.25
| Do. Do. 1 inch (25mm) dia. | 120 | Rft | 42.23 | 5067.6
| Do. Do. 1-1/4 inch (32 mm) dia.. | 150 | Rft | 64.23 | 9634.5
| Do. Do. 1-1/2 inch (40 mm) dia.. | 150 | Rft | 82.1 | 12315
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 120 | R.ft | 67.8153 | 8137.8317
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 60 | R.ft | 88.2753 | 5296.5158
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 50 | R.ft | 127.734 | 6386.7012
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 10 | Each | 882.9832 | 8829.832
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 6 | Each | 17442.4785 | 104654.8708
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 2500 | %Cft | 599.7012 | 14992.5295
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe.. | 450 | R.ft. | 250.26 | 112617
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 20 | Cft. | 664.8382 | 13296.764
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 10 | Each | 1500 | 15000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 4 | Each | 105 | 420
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 2 | Each | 125 | 250
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 2 | Each | 215 | 430
| PPRC Ball Valve 20 mm. | 2 | Each | 643.5 | 1287
| PPRC Ball Valve 25 mm. | 2 | Each | 783.75 | 1567.5
| TOTAL OF SUB HEAD C |  |  |  | 687586.435
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (FIRST FLOOR EYE CLINIC )
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (GROUND FLOOR CONSULTANT"S CLINIC REMAINING WORKS )
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 200 | Rft | 25 | 5000
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 0 | 100 Sq.ft. | 12000 | 0
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 50 | Sft | 700 | 35000
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 250 | Rft | 140 | 35000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 250 | Rft | 225 | 56250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 40 | R.ft | 200.08 | 8003.2
| 8 inch dia | 0 | R.ft | 352.16 | 0
| 12 inch dia | 0 | R.ft | 719.35 | 0
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 30500 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 100 | Rft | 310 | 31000
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 4 | No | 350 | 1400
| Total Of Non Schedule Items |  |  |  | 263153.2
SUMMARY
| Total of Sub Head 'A' | 2336579.1328
| Total of Sub Head 'B' | 135545.28
| Total of Sub Head 'C' | 687586.435
| Total of Non-Schedule Items | 263153.2
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 3422864.0478

## Peer Abad New Golimar Disp
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF Peer abad ( New Golimar Dispensary ) KARACHI
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 8 | Each | 197.795 | 1582.36
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 8 | Each | 127.075 | 1016.6
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 5 | 100 Cft. | 2773.55 | 138.6775
39/123 | Dismantling C.C. floor upto 2" (51 mm) thick in basement, plinth and ground floor including disposing off the material as directed within three chains (91.5 m). | 25 | 100 Cft. | 494.4875 | 123.6219
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 650 | 100 Cft. | 988.975 | 6428.3375
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 25 | 100 Sq.ft. | 372.9375 | 93.2344
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 0 | 100 Cft | 535.0885 | 0
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 10 | 100 Cft | 10085.8049 | 1008.5805
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 10 | 100 Cft. | 18172.93 | 1817.293
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 10 | 100 Cft. | 17514.88 | 1751.488
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 10 | 100 Cft. | 22448.44 | 2244.844
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 20 | 100 Cft. | 20668.6 | 4133.72
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 250 | 100 Cft. | 20143.99 | 50359.975
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 60 | 100 Cft. | 22538.92 | 13523.352
50/114 | Providing and laying reinforced cement concrete using 50 %screened graded bajri & 50 % crushed boulder 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2 ) at 28 days with a mix not leaner than 1:2:4 in straight stairs and landing of required section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 20 | 100 Cft. | 25545.28 | 5109.056
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 20 | 100 Cft. | 25857.43 | 5171.486
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 860 | 100 Cft. | 15033.28 | 129286.208
2/122 | 1/4" (6.4 mm) thick cement plaster 1:4 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 250 | 100 Sq.ft. | 1625.9797 | 4064.9493
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 1800 | 100 Sq.ft. | 1730.7392 | 31153.3053
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 20 | 100 Sq.ft | 2204.0168 | 440.8034
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 120 | 100 Sq.ft | 3075.7 | 3690.84
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required. | 15 | Cft. | 4595.1353 | 68927.0294
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 120 | Sft. | 571.6761 | 68601.1301
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 20 | Sft. | 551.814 | 11036.2799
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 20 | Sq ft | 303.1167 | 6062.3347
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 25 | Sq ft | 503.6173 | 12590.4319
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 25 | Sq ft | 419.1321 | 10478.3036
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 250 | Sq ft | 91.9382 | 22984.5426
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required. | 125 | Sft | 327.3112 | 40913.9046
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 0 | 100 Sq.ft | 124.434 | 0
162/122 | Painting with (ICI) Dulux plastic emulsion paint VIP of approved shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor. | 0 | 100 Sq.ft | 2742.0796 | 0
160/122 | Painting wood work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor. | 650 | 100 Sq.ft | 2585.2182 | 16803.9184
159/122 | Painting iron work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor. | 150 | 100 Sq.ft | 2776.6219 | 4164.9329
172/122 | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | 0 | 100 Sq.ft | 1406.8847 | 0
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor. | 5000 | 100 Sq.ft. | 560.9844 | 28049.2188
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 16500 | 100 Sq.ft. | 505.095 | 83340.675
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 250 | 100 Sq.ft. | 924.3325 | 2310.8313
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 120 | 100 Sq.ft. | 955.7145 | 1146.8574
99/119 | Providing and fixing fully glazed Bronze anodized or powder coated aluminium Sliding windows as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators) deluxe model box section 95mm x 30mm and 1.6mm thick including the cost of aluminium netting ,fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 567.543 | 34052.58
108/119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Hinged door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators), Economy model section, 76.2mm x 30mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 80 | Sq.ft. | 440.7402 | 35259.2196
120 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 260 | Sq.ft. | 106.1059 | 27587.5228
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 650 | 100 Sq.ft. | 3053.2494 | 19846.1212
157 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 450 | 100 Rft. | 1368.1642 | 6156.7388
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors. | 650 | Sq.ft. | 103.0965 | 67012.725
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor. | 80 | Sqft | 363.11 | 29048.796
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 0 | Cwt | 9607.9425 | 0
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 60 | 100 Sq.ft | 12123.2262 | 7273.9357
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 80 | 100 Sq.ft | 8408.2262 | 6726.5809
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension. | 0 | Cwt. | 6249.9391 | 0
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 15 | Rft | 157.1211 | 2356.816
119/25 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | 20 | Sq.ft. | 494.9753 | 9899.5063
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 2 | Cwt. | 7634.0786 | 15268.1573
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 10 | Each | 2531.555 | 25315.55
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 5 | Each | 1063.8056 | 5319.028
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 10 | Each | 59.6369 | 596.3685
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm. | 10 | Each | 382.4221 | 3824.2208
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 10 | Rft. | 121.8152 | 1218.152
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge. | 2 | Each | 2420.5025 | 4841.005
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size. | 4 | Each | 407.2754 | 1629.1015
3 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent. | 60 | 100 Sq.ft. | 2659.7875 | 1595.8725
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 6 | Ib | 145.396 | 872.376
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete. | 10 | Rft. | 107.7375 | 1077.375
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete. | 120 | Rft. | 210.5485 | 25265.825
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe. | 10 | Each | 159.1642 | 1591.642
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete. | 5 | Each | 629.85 | 3149.25
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 2 | Lbs. | 66.0667 | 132.1334
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 0 | % Cft | 42.3057 | 0
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor. | 50 | 100 Sq.ft. | 1878.9641 | 939.482
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors. | 200 | Rft. | 9.6687 | 1933.75
63/117 | Providing and laying floor of 6mm (approx: 1/4") thick coloured glazed tiles 12" x 12" (304mm x 304mm) of master make (Pakistani) first grade in ground floor laid over 1" (25mm) thick cement mortar 1:2 (1 cement and 2 sand) including jointing and washing the tiles with white cement slurry a matching colour (by using pigment in white cement) and curing etc. complete. | 5500 | 100 Sq.ft. | 18359.6026 | 1009778.1429
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 5 | Each | 54.36 | 271.8
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 2 | Each | 84.74 | 169.48
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 5 | lbs | 76.49 | 382.45
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 0 | cwt | 7997.6 | 0
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 0 | rft | 333.08 | 0
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height. | 560 | Sq. In | 0.95 | 532
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete. | 0 | cwt | 6074.4 | 0
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 45 | Sqft | 225.13 | 10130.85
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor. | 20 | 100Rft | 2258.58 | 451.716
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor. | 25 | 100Rft | 1392.7559 | 348.189
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 50 | 100 Sq.ft | 135.06 | 67.53
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 0 | 100 Sq.ft | 284.54 | 0
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 60 | 100 Sq.ft | 2371.9061 | 1423.1436
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 60 | Sft | 96.8 | 5808
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor. | 0 | 100 Sft | 727.47 | 0
228/125 | Easing doors, windows and ventilators in all floors. | 20 | Each | 43.1 | 862
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 2000 | Sft | 71.69 | 143380
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 650 | 100 Sft. | 9097.3098 | 59132.5134
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete. | 0 | cwt | 5988.48 | 0
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 6500 | 100 Sq.ft. | 139.9325 | 9095.6125
30/125 | Plastering 1" (25 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 50 | 100 Sq.ft. | 2986.91 | 1493.455
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required. | 350 | SQFT | 48.02 | 16807
| TOTAL OF SUB -HEAD A |  |  |  | 2336579.1328
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF Peer abad ( New Golimar Dispensary ) KARACHI
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired. | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
5/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 4800 | 100 Cft | 2823.86 | 135545.28
| TOTAL OF SUB HEAD B |  |  |  | 135545.28
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF Peer abad ( New Golimar Dispensary ) KARACHI
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 10 | Each | 4601.3 | 46013
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4. | 10 | Each | 4628.14 | 46281.4
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal. | 10 | Each | 863.83 | 8638.3
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 10 | Each | 389.752 | 3897.52
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 10 | Each | 6611.132 | 66111.32
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 5 | Each | 534.3008 | 2671.504
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 5 | Each | 720.94 | 3604.7
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 10 | Each | 279.75 | 2797.5
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 40 | Rft | 68.32 | 2732.8
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 10 | Rft | 85.26 | 852.6
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 24 | Rft | 120.35 | 2888.4
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 12 | Rft | 158.07 | 1896.84
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 15 | Rft | 170.58 | 2558.7
| Do. 2inches (50 mm) dia pipe (ILLM). | 10 | Rft | 232.03 | 2320.3
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 25 | Rft | 35.21 | 880.25
| Do. Do. 1 inch (25mm) dia. | 120 | Rft | 42.23 | 5067.6
| Do. Do. 1-1/4 inch (32 mm) dia.. | 150 | Rft | 64.23 | 9634.5
| Do. Do. 1-1/2 inch (40 mm) dia.. | 150 | Rft | 82.1 | 12315
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 120 | R.ft | 67.8153 | 8137.8317
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 60 | R.ft | 88.2753 | 5296.5158
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 50 | R.ft | 127.734 | 6386.7012
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 10 | Each | 882.9832 | 8829.832
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 6 | Each | 17442.4785 | 104654.8708
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m). | 2500 | %Cft | 599.7012 | 14992.5295
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe. | 450 | R.ft. | 250.26 | 112617
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 20 | Cft. | 664.8382 | 13296.764
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 10 | Each | 1500 | 15000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 4 | Each | 105 | 420
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 2 | Each | 125 | 250
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 2 | Each | 215 | 430
| PPRC Ball Valve 20 mm. | 2 | Each | 643.5 | 1287
| PPRC Ball Valve 25 mm. | 2 | Each | 783.75 | 1567.5
| TOTAL OF SUB HEAD C |  |  |  | 687586.435
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF Peer abad ( New Golimar Dispensary ) KARACHI
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 200 | Rft | 25 | 5000
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 0 | 100 Sq.ft. | 12000 | 0
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 50 | Sft | 700 | 35000
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 250 | Rft | 140 | 35000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 250 | Rft | 225 | 56250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 40 | R.ft | 200.08 | 8003.2
| 8 inch dia | 0 | R.ft | 352.16 | 0
| 12 inch dia | 0 | R.ft | 719.35 | 0
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 30500 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 100 | Rft | 310 | 31000
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 4 | No | 350 | 1400
| Total Of Non Schedule Items |  |  |  | 263153.2
SUMMARY
| Total of Sub Head 'A' | 2336579.1328
| Total of Sub Head 'B' | 135545.28
| Total of Sub Head 'C' | 687586.435
| Total of Non-Schedule Items | 263153.2
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 3422864.0478

## Lines Area Consultant's
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (GROUND FLOOR CONSULTANT"S CLINIC REMAINING WORKS )
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 3 | Each | 197.795 | 593.385
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 3 | Each | 127.075 | 381.225
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 25 | 100 Cft. | 2773.55 | 693.3875
39/123 | Dismantling C.C. floor upto 2" (51 mm) thick in basement, plinth and ground floor including disposing off the material as directed within three chains (91.5 m). | 350 | 100 Cft. | 494.4875 | 1730.7062
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 60 | 100 Cft. | 988.975 | 593.385
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 60 | 100 Sq.ft. | 372.9375 | 223.7625
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 650 | 100 Cft | 535.0885 | 3478.0752
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 60 | 100 Cft | 10085.8049 | 6051.4829
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 40 | 100 Cft. | 18172.93 | 7269.172
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 180 | 100 Cft. | 17514.88 | 31526.784
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 160 | 100 Cft. | 22448.44 | 35917.504
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 450 | 100 Cft. | 20668.6 | 93008.7
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 1200 | 100 Cft. | 20143.99 | 241727.88
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 120 | 100 Cft. | 22538.92 | 27046.704
50/114 | Providing and laying reinforced cement concrete using 50 %screened graded bajri & 50 % crushed boulder 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2 ) at 28 days with a mix not leaner than 1:2:4 in straight stairs and landing of required section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 30 | 100 Cft. | 25545.28 | 7663.584
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 20 | 100 Cft. | 25857.43 | 5171.486
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 560 | 100 Cft. | 15033.28 | 84186.368
2/122 | 1/4" (6.4 mm) thick cement plaster 1:4 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 2250 | 100 Sq.ft. | 1625.9797 | 36584.544
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 2800 | 100 Sq.ft. | 1730.7392 | 48460.6971
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 120 | 100 Sq.ft | 2204.0168 | 2644.8201
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 120 | 100 Sq.ft | 3075.7 | 3690.84
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 3 | Cft. | 4595.1353 | 13785.4059
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 80 | Sft. | 571.6761 | 45734.0868
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 75 | Sft. | 551.814 | 41386.0495
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 150 | Sq ft | 303.1167 | 45467.5104
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 140 | Sq ft | 503.6173 | 70506.4186
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 180 | Sq ft | 419.1321 | 75443.7857
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 250 | Sq ft | 91.9382 | 22984.5426
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 125 | Sft | 327.3112 | 40913.9046
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 0 | 100 Sq.ft | 124.434 | 0
162/122 | Painting with (ICI) Dulux plastic emulsion paint VIP of approved shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor . | 0 | 100 Sq.ft | 2742.0796 | 0
160/122 | Painting wood work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 450 | 100 Sq.ft | 2585.2182 | 11633.482
159/122 | Painting iron work with synthetic enamel paint of approved make and shade two coats over and including the cost of one priming coat complete at any height in any floor . | 150 | 100 Sq.ft | 2776.6219 | 4164.9329
172/122 | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | 0 | 100 Sq.ft | 1406.8847 | 0
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 2500 | 100 Sq.ft. | 560.9844 | 14024.6094
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 6500 | 100 Sq.ft. | 505.095 | 32831.175
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 250 | 100 Sq.ft. | 924.3325 | 2310.8313
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 120 | 100 Sq.ft. | 955.7145 | 1146.8574
99/119 | Providing and fixing fully glazed Bronze anodized or powder coated aluminium Sliding windows as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators) deluxe model box section 95mm x 30mm and 1.6mm thick including the cost of aluminium netting ,fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 140 | Sq.ft. | 567.543 | 79456.0201
108/119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Hinged door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P (fixing through their approved fabricators), Economy model section, 76.2mm x 30mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 180 | Sq.ft. | 440.7402 | 79333.2441
120 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 310 | Sq.ft. | 106.1059 | 32892.8157
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 1250 | 100 Sq.ft. | 3053.2494 | 38165.6178
157 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 500 | Sft | 74.8883 | 37444.153
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 1450 | 100 Rft. | 1368.1642 | 19838.3805
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 650 | Sq.ft. | 103.0965 | 67012.725
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 80 | Sqft | 363.11 | 29048.796
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 0 | Cwt | 9607.9425 | 0
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 60 | 100 Sq.ft | 12123.2262 | 7273.9357
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 80 | 100 Sq.ft | 8408.2262 | 6726.5809
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 40 | Cwt. | 6249.9391 | 249997.5624
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 15 | Rft | 157.1211 | 2356.816
119/25 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor.. | 20 | Sq.ft. | 494.9753 | 9899.5063
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 2 | Cwt. | 7634.0786 | 15268.1573
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 5 | Each | 2531.555 | 12657.775
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 5 | Each | 1063.8056 | 5319.028
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 20 | Each | 88.5392 | 1770.7846
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 10 | Each | 59.6369 | 596.3685
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 20 | Each | 382.4221 | 7648.4417
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 20 | Rft. | 121.8152 | 2436.304
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 2 | Each | 2420.5025 | 4841.005
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 4 | Each | 407.2754 | 1629.1015
3 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 950 | 100 Sq.ft. | 2659.7875 | 25267.9808
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 150 | Ib | 145.396 | 21809.4
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 10 | Rft. | 107.7375 | 1077.375
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 120 | Rft. | 210.5485 | 25265.825
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 10 | Each | 159.1642 | 1591.642
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 5 | Each | 629.85 | 3149.25
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 2 | Lbs. | 66.0667 | 132.1334
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 0 | % Cft | 42.3057 | 0
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 50 | 100 Sq.ft. | 1878.9641 | 939.482
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 200 | Rft. | 9.6687 | 1933.75
63/117 | Providing and laying floor of 6mm (approx: 1/4") thick coloured glazed tiles 12" x 12" (304mm x 304mm) of master make (Pakistani) first grade in ground floor laid over 1" (25mm) thick cement mortar 1:2 (1 cement and 2 sand) including jointing and washing the tiles with white cement slurry a matching colour (by using pigment in white cement) and curing etc. complete. | 5500 | 100 Sq.ft. | 18359.6026 | 1009778.1429
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 5 | Each | 54.36 | 271.8
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 2 | Each | 84.74 | 169.48
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 5 | lbs | 76.49 | 382.45
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 20 | cwt | 7997.6 | 159952
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 50 | rft | 333.08 | 16654
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 560 | Sq. In | 0.95 | 532
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 0 | cwt | 6074.4 | 0
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 45 | Sqft | 225.13 | 10130.85
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 20 | 100Rft | 2258.58 | 451.716
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 25 | 100Rft | 1392.7559 | 348.189
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 450 | 100 Sq.ft | 135.06 | 607.77
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 50 | 100 Sq.ft | 284.54 | 142.27
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 60 | 100 Sq.ft | 2371.9061 | 1423.1436
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 60 | Sft | 96.8 | 5808
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 260 | 100 Sft | 727.47 | 1891.422
228/125 | Easing doors, windows and ventilators in all floors. | 20 | Each | 43.1 | 862
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 5000 | Sft | 71.69 | 358450
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 30 | lbs | 180.48 | 5414.4
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 1000 | 100 Sft. | 9097.3098 | 90973.0975
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 10 | cwt | 5988.48 | 59884.8
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 200 | 100 Sq.ft. | 139.9325 | 279.865
30/125 | Plastering 1" (25 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 50 | 100 Sq.ft. | 2986.91 | 1493.455
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 350 | SQFT | 48.02 | 16807
| TOTAL OF SUB -HEAD A |  |  |  | 3691686.7973
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (GROUND FLOOR CONSULTANT"S CLINIC REMAINING WORKS )
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 50 | 100 Sq.ft. | 3840.8809 | 1920.4405
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 45 | 100 Sq ft | 12266.26 | 5519.817
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 1500 | 100 Sqft | 6102.5179 | 91537.7691
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 460 | 100 Rft. | 13968.6715 | 64255.8888
5/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 480 | 100 Cft | 2823.86 | 13554.528
| TOTAL OF SUB HEAD B |  |  |  | 176788.4433
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (GROUND FLOOR CONSULTANT"S CLINIC REMAINING WORKS )
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4.. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4.. | 10 | Each | 4601.3 | 46013
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4.. | 10 | Each | 4628.14 | 46281.4
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 10 | Each | 863.83 | 8638.3
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 10 | Each | 389.752 | 3897.52
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 10 | Each | 6611.132 | 66111.32
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 5 | Each | 534.3008 | 2671.504
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 5 | Each | 720.94 | 3604.7
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 10 | Each | 279.75 | 2797.5
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 40 | Rft | 68.32 | 2732.8
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 10 | Rft | 85.26 | 852.6
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 24 | Rft | 120.35 | 2888.4
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 12 | Rft | 158.07 | 1896.84
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 15 | Rft | 170.58 | 2558.7
| Do. 2inches (50 mm) dia pipe (ILLM). | 10 | Rft | 232.03 | 2320.3
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 25 | Rft | 35.21 | 880.25
| Do. Do. 1 inch (25mm) dia. | 120 | Rft | 42.23 | 5067.6
| Do. Do. 1-1/4 inch (32 mm) dia.. | 150 | Rft | 64.23 | 9634.5
| Do. Do. 1-1/2 inch (40 mm) dia.. | 150 | Rft | 82.1 | 12315
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 120 | R.ft | 67.8153 | 8137.8317
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 60 | R.ft | 88.2753 | 5296.5158
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 50 | R.ft | 127.734 | 6386.7012
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 10 | Each | 882.9832 | 8829.832
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 6 | Each | 17442.4785 | 104654.8708
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m). | 2500 | %Cft | 599.7012 | 14992.5295
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe. | 450 | R.ft. | 250.26 | 112617
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 20 | Cft. | 664.8382 | 13296.764
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 10 | Each | 1500 | 15000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 4 | Each | 105 | 420
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 2 | Each | 125 | 250
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 2 | Each | 215 | 430
| PPRC Ball Valve 20 mm. | 2 | Each | 643.5 | 1287
| PPRC Ball Valve 25 mm. | 2 | Each | 783.75 | 1567.5
| TOTAL OF SUB HEAD C |  |  |  | 687586.435
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (GROUND FLOOR CONSULTANT"S CLINIC REMAINING WORKS )
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 200 | Rft | 25 | 5000
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 560 | 100 Sq.ft. | 12000 | 67200
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 50 | Sft | 700 | 35000
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 250 | Rft | 140 | 35000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 250 | Rft | 225 | 56250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 40 | R.ft | 200.08 | 8003.2
| 8 inch dia | 40 | R.ft | 352.16 | 14086.4
| 12 inch dia | 80 | R.ft | 719.35 | 57548
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 2000 | Sft | 10 | 20000
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 30500 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 100 | Rft | 310 | 31000
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 4 | No | 350 | 1400
| Total Of Non Schedule Items |  |  |  | 421987.6
SUMMARY
| Total of Sub Head 'A' | 3691686.7973
| Total of Sub Head 'B' | 176788.4433
| Total of Sub Head 'C' | 687586.435
| Total of Non-Schedule Items | 421987.6
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 4978049.2756

## Sukkur Disp
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- REPAIR/MAINTENANCE & RENNOVATION OF DISPENSARY AT SITE AREA SUKKUR
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 4 | Each | 197.795 | 791.18
| b) First Floor | 6 | Each | 211.61 | 1269.66
| c) Second Floor | 0 | Each | 225.42 | 0
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 4 | Each | 127.075 | 508.3
| b) First Floor | 6 | Each | 137.58 | 825.48
| c) Second Floor | 0 | Each | 148.08 | 0
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 18 | Cft. | 4595.1353 | 82712.4352
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 20 | 100 Cft. | 2773.55 | 554.71
| b) First Floor | 40 | 100 Cft. | 3024.39 | 1209.756
| c) Second Floor | 5 | 100 Cft. | 3253.68 | 162.684
| d) Third Floor | 0 | 100 Cft. | 3482.97 | 0
9/123 | Dismantling burnt brick masonry in lime or cement mortar foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed within three chains (91.5 m). | 50 | 100 Cft. | 988.975 | 494.4875
| b) First Floor | 650 | 100 Cft. | 1103.9 | 7175.35
| c) Second Floor | 150 | 100 Cft. | 1385.51 | 2078.265
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 0 | 100 Cft. | 988.975 | 0
| b) First Floor | 0 | 100 Cft. | 1239.82 | 0
| c) Second Floor | 0 | 100 Cft. | 1469.11 | 0
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 0 | 100 Cft | 535.0885 | 0
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 25 | 100 Cft | 10085.8049 | 2521.4512
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 25 | 100 Cft. | 18172.93 | 4543.2325
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 10 | 100 Cft. | 17514.88 | 1751.488
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 10 | 100 Cft. | 22448.44 | 2244.844
| b) First Floor | 140 | 100 Cft. | 23397.64 | 32756.696
| c) Second Floor | 70 | 100 Cft. | 24149.14 | 16904.398
| d) Third Floor | 0 | 100 Cft. | 24900.64 | 0
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 20 | 100 Cft. | 20668.6 | 4133.72
| b) First Floor | 410 | 100 Cft. | 21617.8 | 88632.98
| c) Second Floor | 140 | 100 Cft. | 22369.25 | 31316.95
| d) Third Floor | 0 | 100 Cft. | 23120.7 | 0
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 20 | 100 Cft. | 20143.99 | 4028.798
| b) First Floor | 650 | 100 Cft. | 21093.19 | 137105.735
| c) Second Floor | 1250 | 100 Cft. | 21844.64 | 273058
| d) Third Floor | 0 | 100 Cft. | 22596.09 | 0
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 10 | 100 Cft. | 22538.92 | 2253.892
| b) First Floor | 55 | 100 Cft. | 23488.12 | 12918.466
| c) Second Floor | 10 | 100 Cft. | 24239.57 | 2423.957
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 10 | 100 Cft. | 25857.43 | 2585.743
24/112 | Providing and laying first class solid burnt brick masonry set in cement mortar 1:6 in straight or curved walls 9 to 13-1/2 inches (229 mm to 343 mm) thick including scaffolding, raking, out joints and curing etc. complete in ground floor superstructure . | 250 | 100 Cft. | 21905.3463 | 54763.3657
| b) First Floor | 1500 | 100 Cft. | 22096.78 | 331451.7
| c) Second Floor | 250 | 100 Cft. | 22776.26 | 56940.65
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 500 | 100 Cft. | 1730.7392 | 8653.6959
| b) First Floor | 4000 | 100 Cft. | 1935.9 | 77436
| c) Second Floor | 650 | 100 Cft. | 2066.36 | 13431.34
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension. | 10 | Cwt. | 6249.9391 | 62499.3906
| b) First Floor | 120 | Cwt. | 6323.42 | 758810.4
| c) Second Floor | 60 | Cwt. | 6396.9 | 383814
| d) Third Floor | 0 | Cwt. | 6470.38 | 0
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 0 | 100 Cft. | 15033.28 | 0
| b) First Floor | 0 | 100 Cft. | 15857.05 | 0
| c) Second Floor | 0 | 100 Cft. | 16536.53 | 0
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 60 | 100 Sq.ft | 2204.0168 | 1322.4101
| b) First Floor | 150 | 100 Sq.ft | 2328.9 | 3493.35
| c) Second Floor | 0 | 100 Sq.ft | 2406.95 | 0
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 150 | 100 Sq.ft | 2328.1361 | 3492.2042
| b) First Floor | 560 | 100 Sq.ft | 2453.02 | 13736.912
| c) Second Floor | 60 | 100 Sq.ft | 2531.07 | 1518.642
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 40 | 100 Sq.ft | 3075.7 | 1230.28
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor. | 10500 | 100 Sq.ft. | 560.9844 | 58903.3594
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 120 | Sft. | 571.6761 | 68601.1301
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 25 | Sft. | 551.814 | 13795.3498
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required. | 25 | Sq ft | 303.1167 | 7577.9184
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 25 | Sq ft | 503.6173 | 12590.4319
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 60 | Sq ft | 419.1321 | 25147.9286
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 675 | Sq ft | 91.9382 | 62058.2651
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required. | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required. | 50 | Sft | 327.3112 | 16365.5619
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 6500 | 100 Sq.ft. | 505.095 | 32831.175
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 2650 | 100 Sq.ft | 789.1413 | 20912.2431
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor. | 3650 | 100 Sq.ft. | 751.51 | 27430.115
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 160 | 100 Sft. | 415.4358 | 664.6973
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | 85 | Sft | 494.9753 | 42072.9019
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 330.2261 | 19813.5648
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sft | 629.3167 | 37759.002
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 447.0099 | 26820.5966
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 550 | Sq.ft. | 106.1059 | 58358.2213
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 460 | 100 Sq.ft. | 3053.2494 | 14044.9473
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 3200 | 100 Sqft | 17882.3933 | 572236.5842
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 200 | 100 Rft. | 1368.1642 | 2736.3283
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 650 | 100 Sq.ft. | 924.3325 | 6008.1613
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1250 | 100 Sq.ft. | 955.7145 | 11946.4312
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 6500 | 100 Sq.ft. | 124.434 | 8088.21
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors. | 1250 | Sq.ft. | 103.0965 | 128870.625
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor. | 125 | Sqft | 363.11 | 45388.7438
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 15 | Cwt | 9607.9425 | 144119.1368
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 50 | 100 Sq.ft | 12123.2262 | 6061.6131
| b) First Floor | 25 | 100 Sq.ft | 12365.19 | 3091.2975
| c) Second Floor | 25 | 100 Sq.ft | 12653.98 | 3163.495
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 650 | 100 Sq.ft | 8408.2262 | 54653.47
| b) First Floor | 850 | 100 Sq.ft | 8650.19 | 73526.615
| c) Second Floor | 85 | 100 Sq.ft | 8938.98 | 7598.133
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 8 | Cwt. | 7634.0786 | 61072.629
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 10 | Each | 2531.555 | 25315.55
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m). | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 500 | 100 Sq.ft. | 602.78 | 3013.9
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 25 | Each | 1063.8056 | 26595.14
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm. | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge. | 5 | Each | 2420.5025 | 12102.5125
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size. | 3 | Each | 407.2754 | 1221.8261
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent. | 2500 | 100 Sq.ft. | 2659.7875 | 66494.6864
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 150 | Ib | 145.396 | 21809.4
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete. | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete. | 120 | Rft. | 210.5485 | 25265.825
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe. | 10 | Each | 159.1642 | 1591.642
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete. | 10 | Each | 629.85 | 6298.5
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 150 | % Cft | 42.3057 | 63.4586
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor. | 160 | 100 Sq.ft. | 1878.9641 | 3006.3426
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors. | 300 | Rft. | 9.6687 | 2900.625
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 2 | cwt | 7997.6 | 15995.2
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 25 | rft | 333.08 | 8327
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height. | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete. | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor. | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor. | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 150 | 100 Sq.ft | 135.06 | 202.59
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 150 | 100 Sq.ft | 284.54 | 426.81
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 250 | 100 Sq.ft | 2371.9061 | 5929.7651
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 250 | 100 Sft | 727.47 | 1818.675
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 450 | Sft | 71.69 | 32260.5
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 650 | 100 Sft. | 9097.3098 | 59132.5134
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 50 | 100 Sq.ft | 43.4293 | 21.7146
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 500 | 100 Sq.ft | 110.385 | 551.925
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 5 | cwt | 5988.48 | 29942.4
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 20000 | 100 Sq.ft. | 139.9325 | 27986.5
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required. | 60 | SQFT | 48.02 | 2881.2
| TOTAL OF SUB -HEAD A ( AS PER PAK PWD SCH. OF RATES 2012 |  |  |  | 4730351.6731
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF DISPENSARY AT SITE AREA SUKKUR
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired. | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 3600 | 100 Cft | 2823.86 | 101658.96
| TOTAL OF SUB HEAD B |  |  |  | 101658.96
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF DISPENSARY AT SITE AREA SUKKUR
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 8 | Each | 4601.3 | 36810.4
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4. | 8 | Each | 4628.14 | 37025.12
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal. | 8 | Each | 863.83 | 6910.64
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 10 | Each | 389.752 | 3897.52
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 15 | Each | 279.75 | 4196.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 40 | Rft | 68.32 | 2732.8
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 45 | Rft | 85.26 | 3836.7
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 30 | Rft | 120.35 | 3610.5
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 20 | Rft | 158.07 | 3161.4
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 125 | Rft | 35.21 | 4401.25
| Do. Do. 1 inch (25mm) dia. | 135 | Rft | 42.23 | 5701.05
| Do. Do. 1-1/4 inch (32 mm) dia.. | 125 | Rft | 64.23 | 8028.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 250 | Rft | 82.1 | 20525
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 250 | R.ft | 67.8153 | 16953.816
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 45 | R.ft | 88.2753 | 3972.3869
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 55 | R.ft | 127.734 | 7025.3713
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 20 | Each | 882.9832 | 17659.664
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 8 | Each | 17442.4785 | 139539.8277
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m). | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe. | 150 | R.ft. | 250.26 | 37539
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 6 | Each | 1500 | 9000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 6 | Each | 105 | 630
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 5 | Each | 215 | 1075
| PPRC Ball Valve 20 mm. | 5 | Each | 643.5 | 3217.5
| PPRC Ball Valve 25 mm. | 2 | Each | 783.75 | 1567.5
| TOTAL OF SUB HEAD C |  |  |  | 630656.7724
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF DISPENSARY AT SITE AREA SUKKUR
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 650 | Rft | 25 | 16250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 450 | 100 Sq.ft. | 12000 | 54000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 25 | Sft | 700 | 17500
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 450 | Rft | 140 | 63000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 450 | Rft | 225 | 101250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 75 | R.ft | 200.08 | 15006
| 8 inch dia | 50 | R.ft | 352.16 | 17608
| 12 inch dia | 50 | R.ft | 719.35 | 35967.5
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 33250 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 75 | Rft | 310 | 23250
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total Of Non Schedule Items |  |  |  | 440331.5
SUMMARY
| Total of Sub Head 'A' | 4730351.6731
| Total of Sub Head 'B' | 101658.96
| Total of Sub Head 'C' | 630656.7724
| Total of Non-Schedule Items | 440331.5
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 5902998.9055

## SUKKUR CIRCLE
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CIRCLE OFFICE AT SITE AREA SUKKUR
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 10 | Each | 197.795 | 1977.95
| b) First Floor | 15 | Each | 211.61 | 3174.15
| c) Second Floor | 2 | Each | 225.42 | 450.84
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 10 | Each | 127.075 | 1270.75
| b) First Floor | 15 | Each | 137.58 | 2063.7
| c) Second Floor | 2 | Each | 148.08 | 296.16
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 36 | Cft. | 4595.1353 | 165424.8705
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 20 | 100 Cft. | 2773.55 | 554.71
| b) First Floor | 140 | 100 Cft. | 3024.39 | 4234.146
| c) Second Floor | 650 | 100 Cft. | 3253.68 | 21148.92
| d) Third Floor | 0 | 100 Cft. | 3482.97 | 0
9/123 | Dismantling burnt brick masonry in lime or cement mortar foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed within three chains (91.5 m). | 50 | 100 Cft. | 988.975 | 494.4875
| b) First Floor | 750 | 100 Cft. | 1103.9 | 8279.25
| c) Second Floor | 150 | 100 Cft. | 1385.51 | 2078.265
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 0 | 100 Cft. | 988.975 | 0
| b) First Floor | 0 | 100 Cft. | 1239.82 | 0
| c) Second Floor | 0 | 100 Cft. | 1469.11 | 0
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 0 | 100 Cft | 535.0885 | 0
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 0 | 100 Cft | 10085.8049 | 0
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in foundation basement and plinth | 0 | 100 Cft. | 18172.93 | 0
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 0 | 100 Cft. | 17514.88 | 0
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 0 | 100 Cft. | 22448.44 | 0
| b) First Floor | 40 | 100 Cft. | 23397.64 | 9359.056
| c) Second Floor | 40 | 100 Cft. | 24149.14 | 9659.656
| d) Third Floor | 0 | 100 Cft. | 24900.64 | 0
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 20 | 100 Cft. | 20668.6 | 4133.72
| b) First Floor | 120 | 100 Cft. | 21617.8 | 25941.36
| c) Second Floor | 240 | 100 Cft. | 22369.25 | 53686.2
| d) Third Floor | 120 | 100 Cft. | 23120.7 | 27744.84
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 20 | 100 Cft. | 20143.99 | 4028.798
| b) First Floor | 250 | 100 Cft. | 21093.19 | 52732.975
| c) Second Floor | 2500 | 100 Cft. | 21844.64 | 546116
| d) Third Floor | 300 | 100 Cft. | 22596.09 | 67788.27
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 40 | 100 Cft. | 22538.92 | 9015.568
| b) First Floor | 60 | 100 Cft. | 23488.12 | 14092.872
| c) Second Floor | 10 | 100 Cft. | 24239.57 | 2423.957
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 10 | 100 Cft. | 25857.43 | 2585.743
24/112 | Providing and laying first class solid burnt brick masonry set in cement mortar 1:6 in straight or curved walls 9 to 13-1/2 inches (229 mm to 343 mm) thick including scaffolding, raking, out joints and curing etc. complete in ground floor superstructure. | 150 | 100 Cft. | 21905.3463 | 32858.0194
| b) First Floor | 1200 | 100 Cft. | 22096.78 | 265161.36
| c) Second Floor | 150 | 100 Cft. | 22776.26 | 34164.39
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 500 | 100 Cft. | 1730.7392 | 8653.6959
| b) First Floor | 4000 | 100 Cft. | 1935.9 | 77436
| c) Second Floor | 350 | 100 Cft. | 2066.36 | 7232.26
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension. | 10 | Cwt. | 6249.9391 | 62499.3906
| b) First Floor | 20 | Cwt. | 6323.42 | 126468.4
| c) Second Floor | 60 | Cwt. | 6396.9 | 383814
| d) Third Floor | 20 | Cwt. | 6470.38 | 129407.6
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 0 | 100 Cft. | 15033.28 | 0
| b) First Floor | 0 | 100 Cft. | 15857.05 | 0
| c) Second Floor | 0 | 100 Cft. | 16536.53 | 0
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 60 | 100 Sq.ft | 2204.0168 | 1322.4101
| b) First Floor | 1550 | 100 Sq.ft | 2328.9 | 36097.95
| c) Second Floor | 550 | 100 Sq.ft | 2406.95 | 13238.225
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 50 | 100 Sq.ft | 2328.1361 | 1164.0681
| b) First Floor | 850 | 100 Sq.ft | 2453.02 | 20850.67
| c) Second Floor | 450 | 100 Sq.ft | 2531.07 | 11389.815
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 140 | 100 Sq.ft | 3075.7 | 4305.98
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 12500 | 100 Sq.ft. | 560.9844 | 70123.0469
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 120 | Sft. | 571.6761 | 68601.1301
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required. | 25 | Sft. | 551.814 | 13795.3498
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 25 | Sq ft | 303.1167 | 7577.9184
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required. | 25 | Sq ft | 503.6173 | 12590.4319
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required. | 60 | Sq ft | 419.1321 | 25147.9286
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 275 | Sq ft | 91.9382 | 25282.9969
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required. | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required. | 50 | Sft | 327.3112 | 16365.5619
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 8500 | 100 Sq.ft. | 505.095 | 42933.075
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 2550 | 100 Sq.ft | 789.1413 | 20123.1019
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor. | 3650 | 100 Sq.ft. | 751.51 | 27430.115
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 160 | 100 Sft. | 415.4358 | 664.6973
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | 85 | Sft | 494.9753 | 42072.9019
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 330.2261 | 19813.5648
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sft | 629.3167 | 37759.002
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 447.0099 | 26820.5966
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 550 | Sq.ft. | 106.1059 | 58358.2213
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 1550 | 100 Sq.ft. | 3053.2494 | 47325.366
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 2500 | 100 Sqft | 17882.3933 | 447059.8314
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 200 | 100 Rft. | 1368.1642 | 2736.3283
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 450 | 100 Sq.ft. | 924.3325 | 4159.4963
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1250 | 100 Sq.ft. | 955.7145 | 11946.4312
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 6500 | 100 Sq.ft. | 124.434 | 8088.21
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors. | 1250 | Sq.ft. | 103.0965 | 128870.625
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor. | 125 | Sqft | 363.11 | 45388.7438
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 15 | Cwt | 9607.9425 | 144119.1368
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 50 | 100 Sq.ft | 12123.2262 | 6061.6131
| b) First Floor | 25 | 100 Sq.ft | 12365.19 | 3091.2975
| c) Second Floor | 25 | 100 Sq.ft | 12653.98 | 3163.495
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 650 | 100 Sq.ft | 8408.2262 | 54653.47
| b) First Floor | 850 | 100 Sq.ft | 8650.19 | 73526.615
| c) Second Floor | 85 | 100 Sq.ft | 8938.98 | 7598.133
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 8 | Cwt. | 7634.0786 | 61072.629
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 10 | Each | 2531.555 | 25315.55
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 6500 | 100 Sq.ft. | 602.78 | 39180.7
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 20 | Each | 1063.8056 | 21276.112
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 5 | Each | 2420.5025 | 12102.5125
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size. | 3 | Each | 407.2754 | 1221.8261
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent. | 6500 | 100 Sq.ft. | 2659.7875 | 172886.1847
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 250 | Ib | 145.396 | 36349
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 120 | Rft. | 210.5485 | 25265.825
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 10 | Each | 159.1642 | 1591.642
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 10 | Each | 629.85 | 6298.5
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 150 | % Cft | 42.3057 | 63.4586
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 160 | 100 Sq.ft. | 1878.9641 | 3006.3426
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 300 | Rft. | 9.6687 | 2900.625
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 2 | cwt | 7997.6 | 15995.2
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 25 | rft | 333.08 | 8327
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height. | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 150 | 100 Sq.ft | 135.06 | 202.59
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 150 | 100 Sq.ft | 284.54 | 426.81
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 250 | 100 Sq.ft | 2371.9061 | 5929.7651
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 250 | 100 Sft | 727.47 | 1818.675
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 450 | Sft | 71.69 | 32260.5
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 650 | 100 Sft. | 9097.3098 | 59132.5134
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 50 | 100 Sq.ft | 43.4293 | 21.7146
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 500 | 100 Sq.ft | 110.385 | 551.925
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 5 | cwt | 5988.48 | 29942.4
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 20000 | 100 Sq.ft. | 139.9325 | 27986.5
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 60 | SQFT | 48.02 | 2881.2
| TOTAL OF SUB -HEAD A |  |  |  | 4536525.9715
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CIRCLE OFFICE AT SITE AREA SUKKUR
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired. | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 3600 | 100 Cft | 2823.86 | 101658.96
| TOTAL OF SUB HEAD B |  |  |  | 101658.96
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CIRCLE OFFICE AT SITE AREA SUKKUR
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 8 | Each | 4601.3 | 36810.4
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4. | 8 | Each | 4628.14 | 37025.12
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal. | 8 | Each | 863.83 | 6910.64
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 10 | Each | 389.752 | 3897.52
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 15 | Each | 279.75 | 4196.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 40 | Rft | 68.32 | 2732.8
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM) | 45 | Rft | 85.26 | 3836.7
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 30 | Rft | 120.35 | 3610.5
| Do.1-1/4 inches (32 mm) dia pipe (ILLM). | 20 | Rft | 158.07 | 3161.4
| Do.1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 125 | Rft | 35.21 | 4401.25
| Do. Do. 1 inch (25mm) dia. | 135 | Rft | 42.23 | 5701.05
| Do. Do. 1-1/4 inch (32 mm) dia.. | 125 | Rft | 64.23 | 8028.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 250 | Rft | 82.1 | 20525
Do. Do. 2 inches (50 mm) dia pipe.
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 250 | R.ft | 67.8153 | 16953.816
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 45 | R.ft | 88.2753 | 3972.3869
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 55 | R.ft | 127.734 | 7025.3713
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 20 | Each | 882.9832 | 17659.664
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 8 | Each | 17442.4785 | 139539.8277
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m). | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe. | 250 | R.ft. | 250.26 | 62565
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 6 | Each | 1500 | 9000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 6 | Each | 105 | 630
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 5 | Each | 215 | 1075
| PPRC Ball Valve 20 mm. | 5 | Each | 643.5 | 3217.5
| PPRC Ball Valve 25 mm. | 2 | Each | 783.75 | 1567.5
| TOTAL OF SUB HEAD C |  |  |  | 655682.7724
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CIRCLE OFFICE AT SITE AREA SUKKUR
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 650 | Rft | 25 | 16250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 450 | 100 Sq.ft. | 12000 | 54000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 0 | Sft | 700 | 0
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 450 | Rft | 140 | 63000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 450 | Rft | 225 | 101250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 75 | R.ft | 200.08 | 15006
| 8 inch dia | 50 | R.ft | 352.16 | 17608
| 12 inch dia | 50 | R.ft | 719.35 | 35967.5
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 33250 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 75 | Rft | 310 | 23250
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total Of Non Schedule Items |  |  |  | 422831.5
SUMMARY
| Total of Sub Head 'A' | 4536525.9715
| Total of Sub Head 'B' | 101658.96
| Total of Sub Head 'C' | 655682.7724
| Total of Non-Schedule Items | 422831.5
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 5716699.2039

## Sukkur City Dis
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY DISPENSARY SUKKUR
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 5 | Each | 197.795 | 988.975
| b) First Floor | 2 | Each | 211.61 | 423.22
| c) Second Floor | 0 | Each | 225.42 | 0
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 5 | Each | 127.075 | 635.375
| b) First Floor | 2 | Each | 137.58 | 275.16
| c) Second Floor | 0 | Each | 148.08 | 0
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required. | 12 | Cft. | 4595.1353 | 55141.6235
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 105 | 100 Cft. | 2773.55 | 2912.2275
| b) First Floor | 50 | 100 Cft. | 3024.39 | 1512.195
| c) Second Floor | 0 | 100 Cft. | 3253.68 | 0
| d) Third Floor | 0 | 100 Cft. | 3482.97 | 0
9/123 | Dismantling burnt brick masonry in lime or cement mortar foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed within three chains (91.5 m). | 250 | 100 Cft. | 988.975 | 2472.4375
| b) First Floor | 60 | 100 Cft. | 1103.9 | 662.34
| c) Second Floor | 0 | 100 Cft. | 1385.51 | 0
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 0 | 100 Cft. | 988.975 | 0
| b) First Floor | 0 | 100 Cft. | 1239.82 | 0
| c) Second Floor | 0 | 100 Cft. | 1469.11 | 0
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 260 | 100 Cft | 535.0885 | 1391.2301
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 0 | 100 Cft | 10085.8049 | 0
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 20 | 100 Cft. | 18172.93 | 3634.586
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 20 | 100 Cft. | 17514.88 | 3502.976
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 25 | 100 Cft. | 22448.44 | 5612.11
| b) First Floor | 0 | 100 Cft. | 23397.64 | 0
| c) Second Floor | 0 | 100 Cft. | 24149.14 | 0
| d) Third Floor | 0 | 100 Cft. | 24900.64 | 0
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 20 | 100 Cft. | 20668.6 | 4133.72
| b) First Floor | 0 | 100 Cft. | 21617.8 | 0
| c) Second Floor | 0 | 100 Cft. | 22369.25 | 0
| d) Third Floor | 0 | 100 Cft. | 23120.7 | 0
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 160 | 100 Cft. | 20143.99 | 32230.384
| b) First Floor | 60 | 100 Cft. | 21093.19 | 12655.914
| c) Second Floor | 0 | 100 Cft. | 21844.64 | 0
| d) Third Floor | 0 | 100 Cft. | 22596.09 | 0
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 240 | 100 Cft. | 22538.92 | 54093.408
| b) First Floor | 60 | 100 Cft. | 23488.12 | 14092.872
| c) Second Floor | 0 | 100 Cft. | 24239.57 | 0
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 50 | 100 Cft. | 25857.43 | 12928.715
24/112 | Providing and laying first class solid burnt brick masonry set in cement mortar 1:6 in straight or curved walls 9 to 13-1/2 inches (229 mm to 343 mm) thick including scaffolding, raking, out joints and curing etc. complete in ground floor superstructure. | 450 | 100 Cft. | 21905.3463 | 98574.0582
| b) First Floor | 200 | 100 Cft. | 22096.78 | 44193.56
| c) Second Floor | 150 | 100 Cft. | 22776.26 | 34164.39
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 500 | 100 Cft. | 1730.7392 | 8653.6959
| b) First Floor | 400 | 100 Cft. | 1935.9 | 7743.6
| c) Second Floor | 0 | 100 Cft. | 2066.36 | 0
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension. | 60 | Cwt. | 6249.9391 | 374996.3436
| b) First Floor | 10 | Cwt. | 6323.42 | 63234.2
| c) Second Floor | 0 | Cwt. | 6396.9 | 0
| d) Third Floor | 0 | Cwt. | 6470.38 | 0
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 0 | 100 Cft. | 15033.28 | 0
| b) First Floor | 0 | 100 Cft. | 15857.05 | 0
| c) Second Floor | 0 | 100 Cft. | 16536.53 | 0
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 560 | 100 Sq.ft | 2204.0168 | 12342.4939
| b) First Floor | 120 | 100 Sq.ft | 2328.9 | 2794.68
| c) Second Floor | 0 | 100 Sq.ft | 2406.95 | 0
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 450 | 100 Sq.ft | 2328.1361 | 10476.6125
| b) First Floor | 220 | 100 Sq.ft | 2453.02 | 5396.644
| c) Second Floor | 0 | 100 Sq.ft | 2531.07 | 0
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 240 | 100 Sq.ft | 3075.7 | 7381.68
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 12500 | 100 Sq.ft. | 560.9844 | 70123.0469
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 40 | Sft. | 571.6761 | 22867.0434
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required. | 25 | Sft. | 551.814 | 13795.3498
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required. | 25 | Sq ft | 303.1167 | 7577.9184
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required. | 0 | Sq ft | 503.6173 | 0
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required. | 60 | Sq ft | 419.1321 | 25147.9286
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 275 | Sq ft | 91.9382 | 25282.9969
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required. | 50 | Sft | 327.3112 | 16365.5619
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 4500 | 100 Sq.ft. | 505.095 | 22729.275
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 1250 | 100 Sq.ft | 789.1413 | 9864.2656
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor. | 1200 | 100 Sq.ft. | 751.51 | 9018.12
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 50 | 100 Sft. | 415.4358 | 207.7179
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | 50 | Sft | 494.9753 | 24748.7658
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 330.2261 | 19813.5648
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sft | 629.3167 | 37759.002
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 447.0099 | 26820.5966
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 220 | Sq.ft. | 106.1059 | 23343.2885
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 1550 | 100 Sq.ft. | 3053.2494 | 47325.366
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 2500 | 100 Sqft | 17882.3933 | 447059.8314
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 200 | 100 Rft. | 1368.1642 | 2736.3283
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 450 | 100 Sq.ft. | 924.3325 | 4159.4963
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1250 | 100 Sq.ft. | 955.7145 | 11946.4312
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 6500 | 100 Sq.ft. | 124.434 | 8088.21
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 1250 | Sq.ft. | 103.0965 | 128870.625
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor. | 125 | Sqft | 363.11 | 45388.7438
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 15 | Cwt | 9607.9425 | 144119.1368
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 50 | 100 Sq.ft | 12123.2262 | 6061.6131
| b) First Floor | 25 | 100 Sq.ft | 12365.19 | 3091.2975
| c) Second Floor | 25 | 100 Sq.ft | 12653.98 | 3163.495
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 650 | 100 Sq.ft | 8408.2262 | 54653.47
| b) First Floor | 0 | 100 Sq.ft | 8650.19 | 0
| c) Second Floor | 0 | 100 Sq.ft | 8938.98 | 0
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 8 | Cwt. | 7634.0786 | 61072.629
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 5 | Each | 2531.555 | 12657.775
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m). | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 3500 | 100 Sq.ft. | 487.86 | 17075.1
| c) Second Floor | 0 | 100 Sq.ft. | 602.78 | 0
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 10 | Each | 1063.8056 | 10638.056
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm. | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge. | 2 | Each | 2420.5025 | 4841.005
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size. | 3 | Each | 407.2754 | 1221.8261
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent. | 3500 | 100 Sq.ft. | 2659.7875 | 93092.561
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 250 | Ib | 145.396 | 36349
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 120 | Rft. | 210.5485 | 25265.825
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 10 | Each | 159.1642 | 1591.642
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 10 | Each | 629.85 | 6298.5
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 150 | % Cft | 42.3057 | 63.4586
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor. | 0 | 100 Sq.ft. | 1878.9641 | 0
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 300 | Rft. | 9.6687 | 2900.625
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 2 | cwt | 7997.6 | 15995.2
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 0 | rft | 333.08 | 0
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 0 | Sqft | 678.32 | 0
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 50 | Sq. In | 0.95 | 47.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor. | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor. | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 150 | 100 Sq.ft | 135.06 | 202.59
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 150 | 100 Sq.ft | 284.54 | 426.81
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 250 | 100 Sq.ft | 2371.9061 | 5929.7651
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor. | 0 | 100 Sft | 727.47 | 0
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 450 | Sft | 71.69 | 32260.5
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 650 | 100 Sft. | 9097.3098 | 59132.5134
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 50 | 100 Sq.ft | 43.4293 | 21.7146
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 500 | 100 Sq.ft | 110.385 | 551.925
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 5 | cwt | 5988.48 | 29942.4
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 20000 | 100 Sq.ft. | 139.9325 | 27986.5
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 60 | SQFT | 48.02 | 2881.2
| TOTAL OF SUB -HEAD A |  |  |  | 2706552.0242
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY DISPENSARY SUKKUR
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 3600 | 100 Cft | 2823.86 | 101658.96
| TOTAL OF SUB HEAD B |  |  |  | 101658.96
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY DISPENSARY SUKKUR
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4.. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4.. | 8 | Each | 4601.3 | 36810.4
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4.. | 8 | Each | 4628.14 | 37025.12
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 8 | Each | 863.83 | 6910.64
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 10 | Each | 389.752 | 3897.52
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
10/302 | Providing and fixing bath room accessories of set of 7 pieces consist of one cosmatic shelf, one towel rod with bracket, one soap dish, one tooth brush holder with glass and cover, one tissue paper holder one double hook one towel ring etc complete of approved quality as per direction of Engineer in-charge. | 10 | Each | 3986.62 | 39866.2
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 15 | Each | 279.75 | 4196.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 40 | Rft | 68.32 | 2732.8
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 45 | Rft | 85.26 | 3836.7
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 30 | Rft | 120.35 | 3610.5
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 20 | Rft | 158.07 | 3161.4
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 125 | Rft | 35.21 | 4401.25
| Do. Do. 1 inch (25mm) dia. | 135 | Rft | 42.23 | 5701.05
| Do. Do. 1-1/4 inch (32 mm) dia.. | 125 | Rft | 64.23 | 8028.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 250 | Rft | 82.1 | 20525
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.)1/2 inch (15mm) dia pipe. | 150 | R.ft | 67.8153 | 10172.2896
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 20 | R.ft | 88.2753 | 1765.5053
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 25 | R.ft | 127.734 | 3193.3506
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 10 | Each | 882.9832 | 8829.832
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 5 | Each | 17442.4785 | 87212.3923
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe. | 150 | R.ft. | 250.26 | 37539
311/1 | Providing and fixing bath room accessories of set of 7 pieces consist of one cosmatic shelf, one towel rod with bracket, one soap dish, one tooth brush holder with glass and cover, one tissue paper holder one double hook one towel ring etc complete of approved quality as per direction of Engineer in-charge. | 0 | Each | 3986.62 | 0
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 6 | Each | 1500 | 9000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 6 | Each | 105 | 630
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 5 | Each | 215 | 1075
| PPRC Ball Valve 20 mm. | 5 | Each | 643.5 | 3217.5
| PPRC Ball Valve 25 mm. | 2 | Each | 783.75 | 1567.5
| TOTAL OF SUB HEAD C |  |  |  | 596545.2763
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY DISPENSARY SUKKUR
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 450 | Rft | 25 | 11250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 45 | 100 Sq.ft. | 12000 | 5400
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 0 | Sft | 700 | 0
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 180 | Rft | 140 | 25200
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 220 | Rft | 225 | 49500
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 75 | R.ft | 200.08 | 15006
| 8 inch dia | 50 | R.ft | 352.16 | 17608
| 12 inch dia | 50 | R.ft | 719.35 | 35967.5
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 33250 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 75 | Rft | 310 | 23250
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total Of Non Schedule Items |  |  |  | 279681.5
SUMMARY
| Total of Sub Head 'A' | 2706552.0242
| Total of Sub Head 'B' | 101658.96
| Total of Sub Head 'C' | 596545.2763
| Total of Non-Schedule Items | 279681.5
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 3684437.7605

## Kotri Hosp
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (MAIN HOSPITAL )
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 4 | Each | 197.795 | 791.18
| b) First Floor | 6 | Each | 211.61 | 1269.66
| c) Second Floor | 0 | Each | 225.42 | 0
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 4 | Each | 127.075 | 508.3
| b) First Floor | 6 | Each | 137.58 | 825.48
| c) Second Floor | 0 | Each | 148.08 | 0
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 18 | Cft. | 4595.1353 | 82712.4352
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 20 | 100 Cft. | 2773.55 | 554.71
| b) First Floor | 40 | 100 Cft. | 3024.39 | 1209.756
| c) Second Floor | 25 | 100 Cft. | 3253.68 | 813.42
| d) Third Floor | 0 | 100 Cft. | 3482.97 | 0
9/123 | Dismantling burnt brick masonry in lime or cement mortar foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed within three chains (91.5 m).. | 50 | 100 Cft. | 988.975 | 494.4875
| b) First Floor | 850 | 100 Cft. | 1103.9 | 9383.15
| c) Second Floor | 150 | 100 Cft. | 1385.51 | 2078.265
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 0 | 100 Cft. | 988.975 | 0
| b) First Floor | 0 | 100 Cft. | 1239.82 | 0
| c) Second Floor | 0 | 100 Cft. | 1469.11 | 0
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 450 | 100 Cft | 535.0885 | 2407.8983
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 125 | 100 Cft | 10085.8049 | 12607.2561
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 25 | 100 Cft. | 18172.93 | 4543.2325
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 20 | 100 Cft. | 17514.88 | 3502.976
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 20 | 100 Cft. | 22448.44 | 4489.688
| b) First Floor | 180 | 100 Cft. | 23397.64 | 42115.752
| c) Second Floor | 60 | 100 Cft. | 24149.14 | 14489.484
| d) Third Floor | 0 | 100 Cft. | 24900.64 | 0
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 20 | 100 Cft. | 20668.6 | 4133.72
| b) First Floor | 410 | 100 Cft. | 21617.8 | 88632.98
| c) Second Floor | 240 | 100 Cft. | 22369.25 | 53686.2
| d) Third Floor | 0 | 100 Cft. | 23120.7 | 0
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 250 | 100 Cft. | 20143.99 | 50359.975
| b) First Floor | 1550 | 100 Cft. | 21093.19 | 326944.445
| c) Second Floor | 850 | 100 Cft. | 21844.64 | 185679.44
| d) Third Floor | 0 | 100 Cft. | 22596.09 | 0
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 10 | 100 Cft. | 22538.92 | 2253.892
| b) First Floor | 55 | 100 Cft. | 23488.12 | 12918.466
| c) Second Floor | 10 | 100 Cft. | 24239.57 | 2423.957
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 30 | 100 Cft. | 25857.43 | 7757.229
24/112 | Providing and laying first class solid burnt brick masonry set in cement mortar 1:6 in straight or curved walls 9 to 13-1/2 inches (229 mm to 343 mm) thick including scaffolding, raking, out joints and curing etc. complete in ground floor superstructure . | 250 | 100 Cft. | 21905.3463 | 54763.3657
| b) First Floor | 2500 | 100 Cft. | 22096.78 | 552419.5
| c) Second Floor | 350 | 100 Cft. | 22776.26 | 79716.91
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 500 | 100 Cft. | 1730.7392 | 8653.6959
| b) First Floor | 5000 | 100 Cft. | 1935.9 | 96795
| c) Second Floor | 650 | 100 Cft. | 2066.36 | 13431.34
1/122 | 1/4" (6.4 mm) thick cement plaster 1:3 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 500 | 100 Cft. | 1710.9844 | 8554.9219
| b) First Floor | 4500 | 100 Cft. | 1864.85 | 83918.25
| c) Second Floor | 450 | 100 Cft. | 2138.58 | 9623.61
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 10 | Cwt. | 6249.9391 | 62499.3906
| b) First Floor | 120 | Cwt. | 6323.42 | 758810.4
| c) Second Floor | 60 | Cwt. | 6396.9 | 383814
| d) Third Floor | 0 | Cwt. | 6470.38 | 0
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 0 | 100 Cft. | 15033.28 | 0
| b) First Floor | 0 | 100 Cft. | 15857.05 | 0
| c) Second Floor | 0 | 100 Cft. | 16536.53 | 0
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 60 | 100 Sq.ft | 2204.0168 | 1322.4101
| b) First Floor | 150 | 100 Sq.ft | 2328.9 | 3493.35
| c) Second Floor | 0 | 100 Sq.ft | 2406.95 | 0
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 150 | 100 Sq.ft | 2328.1361 | 3492.2042
| b) First Floor | 560 | 100 Sq.ft | 2453.02 | 13736.912
| c) Second Floor | 60 | 100 Sq.ft | 2531.07 | 1518.642
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 40 | 100 Sq.ft | 3075.7 | 1230.28
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 10500 | 100 Sq.ft. | 560.9844 | 58903.3594
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 120 | Sft. | 571.6761 | 68601.1301
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 25 | Sft. | 551.814 | 13795.3498
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 25 | Sq ft | 303.1167 | 7577.9184
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 25 | Sq ft | 503.6173 | 12590.4319
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 60 | Sq ft | 419.1321 | 25147.9286
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 675 | Sq ft | 91.9382 | 62058.2651
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 50 | Sft | 327.3112 | 16365.5619
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 6500 | 100 Sq.ft. | 505.095 | 32831.175
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 2650 | 100 Sq.ft | 789.1413 | 20912.2431
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 3650 | 100 Sq.ft. | 751.51 | 27430.115
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 160 | 100 Sft. | 415.4358 | 664.6973
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor.. | 85 | Sft | 494.9753 | 42072.9019
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 330.2261 | 19813.5648
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sft | 629.3167 | 37759.002
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 447.0099 | 26820.5966
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 550 | Sq.ft. | 106.1059 | 58358.2213
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 460 | 100 Sq.ft. | 3053.2494 | 14044.9473
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 3200 | 100 Sqft | 17882.3933 | 572236.5842
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 200 | 100 Rft. | 1368.1642 | 2736.3283
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 650 | 100 Sq.ft. | 924.3325 | 6008.1613
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1250 | 100 Sq.ft. | 955.7145 | 11946.4312
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 6500 | 100 Sq.ft. | 124.434 | 8088.21
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 1250 | Sq.ft. | 103.0965 | 128870.625
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 125 | Sqft | 363.11 | 45388.7438
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 15 | Cwt | 9607.9425 | 144119.1368
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 50 | 100 Sq.ft | 12123.2262 | 6061.6131
| b) First Floor | 25 | 100 Sq.ft | 12365.19 | 3091.2975
| c) Second Floor | 25 | 100 Sq.ft | 12653.98 | 3163.495
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 650 | 100 Sq.ft | 8408.2262 | 54653.47
| b) First Floor | 850 | 100 Sq.ft | 8650.19 | 73526.615
| c) Second Floor | 85 | 100 Sq.ft | 8938.98 | 7598.133
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 8 | Cwt. | 7634.0786 | 61072.629
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 10 | Each | 2531.555 | 25315.55
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 500 | 100 Sq.ft. | 602.78 | 3013.9
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 25 | Each | 1063.8056 | 26595.14
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 5 | Each | 2420.5025 | 12102.5125
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 3 | Each | 407.2754 | 1221.8261
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 2500 | 100 Sq.ft. | 2659.7875 | 66494.6864
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 150 | Ib | 145.396 | 21809.4
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 120 | Rft. | 210.5485 | 25265.825
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 10 | Each | 159.1642 | 1591.642
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 10 | Each | 629.85 | 6298.5
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 150 | % Cft | 42.3057 | 63.4586
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 160 | 100 Sq.ft. | 1878.9641 | 3006.3426
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 300 | Rft. | 9.6687 | 2900.625
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 2 | cwt | 7997.6 | 15995.2
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 25 | rft | 333.08 | 8327
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 150 | 100 Sq.ft | 135.06 | 202.59
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 150 | 100 Sq.ft | 284.54 | 426.81
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 250 | 100 Sq.ft | 2371.9061 | 5929.7651
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 250 | 100 Sft | 727.47 | 1818.675
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 450 | Sft | 71.69 | 32260.5
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 650 | 100 Sft. | 9097.3098 | 59132.5134
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 50 | 100 Sq.ft | 43.4293 | 21.7146
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 500 | 100 Sq.ft | 110.385 | 551.925
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 5 | cwt | 5988.48 | 29942.4
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 20000 | 100 Sq.ft. | 139.9325 | 27986.5
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 60 | SQFT | 48.02 | 2881.2
| TOTAL OF SUB -HEAD A |  |  |  | 5295295.0912
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (MAIN HOSPITAL )
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 3600 | 100 Cft | 2823.86 | 101658.96
| TOTAL OF SUB HEAD B |  |  |  | 101658.96
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (MAIN HOSPITAL )
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4.. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4.. | 8 | Each | 4601.3 | 36810.4
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4.. | 8 | Each | 4628.14 | 37025.12
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 8 | Each | 863.83 | 6910.64
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 10 | Each | 389.752 | 3897.52
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 15 | Each | 279.75 | 4196.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 40 | Rft | 68.32 | 2732.8
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 45 | Rft | 85.26 | 3836.7
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 30 | Rft | 120.35 | 3610.5
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 20 | Rft | 158.07 | 3161.4
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 125 | Rft | 35.21 | 4401.25
| Do. Do. 1 inch (25mm) dia. | 135 | Rft | 42.23 | 5701.05
| Do. Do. 1-1/4 inch (32 mm) dia.. | 125 | Rft | 64.23 | 8028.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 250 | Rft | 82.1 | 20525
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 250 | R.ft | 67.8153 | 16953.816
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 45 | R.ft | 88.2753 | 3972.3869
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 55 | R.ft | 127.734 | 7025.3713
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 20 | Each | 882.9832 | 17659.664
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 10 | Each | 17442.4785 | 174424.7846
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe.. | 250 | R.ft. | 250.26 | 62565
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 6 | Each | 1500 | 9000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 6 | Each | 105 | 630
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 5 | Each | 215 | 1075
| PPRC Ball Valve 20 mm. | 5 | Each | 643.5 | 3217.5
| PPRC Ball Valve 25 mm. | 2 | Each | 783.75 | 1567.5
| TOTAL OF SUB HEAD C |  |  |  | 690567.7293
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (MAIN HOSPITAL )
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 650 | Rft | 25 | 16250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 550 | 100 Sq.ft. | 12000 | 66000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 25 | Sft | 700 | 17500
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 450 | Rft | 140 | 63000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 450 | Rft | 225 | 101250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 75 | R.ft | 200.08 | 15006
| 8 inch dia | 50 | R.ft | 352.16 | 17608
| 12 inch dia | 50 | R.ft | 719.35 | 35967.5
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 33250 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 75 | Rft | 310 | 23250
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total Of Non Schedule Items |  |  |  | 452331.5
SUMMARY
| Total of Sub Head 'A' | 5295295.0912
| Total of Sub Head 'B' | 101658.96
| Total of Sub Head 'C' | 690567.7293
| Total of Non-Schedule Items | 452331.5
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 6539853.2805

## Kotri Doct Res
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (DOCTOR'S RESIDENCE )
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 2 | Each | 197.795 | 395.59
| b) First Floor | 2 | Each | 211.61 | 423.22
| c) Second Floor | 0 | Each | 225.42 | 0
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 2 | Each | 127.075 | 254.15
| b) First Floor | 2 | Each | 137.58 | 275.16
| c) Second Floor | 0 | Each | 148.08 | 0
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 6 | Cft. | 4595.1353 | 27570.8117
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 10 | 100 Cft. | 2773.55 | 277.355
| b) First Floor | 20 | 100 Cft. | 3024.39 | 604.878
| c) Second Floor | 25 | 100 Cft. | 3253.68 | 813.42
| d) Third Floor | 0 | 100 Cft. | 3482.97 | 0
9/123 | Dismantling burnt brick masonry in lime or cement mortar foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed within three chains (91.5 m). | 50 | 100 Cft. | 988.975 | 494.4875
| b) First Floor | 250 | 100 Cft. | 1103.9 | 2759.75
| c) Second Floor | 120 | 100 Cft. | 1385.51 | 1662.612
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 0 | 100 Cft. | 988.975 | 0
| b) First Floor | 0 | 100 Cft. | 1239.82 | 0
| c) Second Floor | 0 | 100 Cft. | 1469.11 | 0
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 150 | 100 Cft | 535.0885 | 802.6327
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 20 | 100 Cft | 10085.8049 | 2017.161
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 25 | 100 Cft. | 18172.93 | 4543.2325
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 20 | 100 Cft. | 17514.88 | 3502.976
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 20 | 100 Cft. | 22448.44 | 4489.688
| b) First Floor | 20 | 100 Cft. | 23397.64 | 4679.528
| c) Second Floor | 0 | 100 Cft. | 24149.14 | 0
| d) Third Floor | 0 | 100 Cft. | 24900.64 | 0
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 20 | 100 Cft. | 20668.6 | 4133.72
| b) First Floor | 60 | 100 Cft. | 21617.8 | 12970.68
| c) Second Floor | 40 | 100 Cft. | 22369.25 | 8947.7
| d) Third Floor | 0 | 100 Cft. | 23120.7 | 0
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 60 | 100 Cft. | 20143.99 | 12086.394
| b) First Floor | 650 | 100 Cft. | 21093.19 | 137105.735
| c) Second Floor | 260 | 100 Cft. | 21844.64 | 56796.064
| d) Third Floor | 0 | 100 Cft. | 22596.09 | 0
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 10 | 100 Cft. | 22538.92 | 2253.892
| b) First Floor | 40 | 100 Cft. | 23488.12 | 9395.248
| c) Second Floor | 10 | 100 Cft. | 24239.57 | 2423.957
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 0 | 100 Cft. | 25857.43 | 0
24/112 | Providing and laying first class solid burnt brick masonry set in cement mortar 1:6 in straight or curved walls 9 to 13-1/2 inches (229 mm to 343 mm) thick including scaffolding, raking, out joints and curing etc. complete in ground floor superstructure. | 250 | 100 Cft. | 21905.3463 | 54763.3657
| b) First Floor | 350 | 100 Cft. | 22096.78 | 77338.73
| c) Second Floor | 350 | 100 Cft. | 22776.26 | 79716.91
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 500 | 100 Cft. | 1730.7392 | 8653.6959
| b) First Floor | 800 | 100 Cft. | 1935.9 | 15487.2
| c) Second Floor | 800 | 100 Cft. | 2066.36 | 16530.88
1/122 | 1/4" (6.4 mm) thick cement plaster 1:3 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 500 | 100 Cft. | 1710.9844 | 8554.9219
| b) First Floor | 600 | 100 Cft. | 1864.85 | 11189.1
| c) Second Floor | 450 | 100 Cft. | 2138.58 | 9623.61
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension. | 10 | Cwt. | 6249.9391 | 62499.3906
| b) First Floor | 40 | Cwt. | 6323.42 | 252936.8
| c) Second Floor | 40 | Cwt. | 6396.9 | 255876
| d) Third Floor | 0 | Cwt. | 6470.38 | 0
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 0 | 100 Cft. | 15033.28 | 0
| b) First Floor | 0 | 100 Cft. | 15857.05 | 0
| c) Second Floor | 0 | 100 Cft. | 16536.53 | 0
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 160 | 100 Sq.ft | 2204.0168 | 3526.4268
| b) First Floor | 450 | 100 Sq.ft | 2328.9 | 10480.05
| c) Second Floor | 0 | 100 Sq.ft | 2406.95 | 0
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 150 | 100 Sq.ft | 2328.1361 | 3492.2042
| b) First Floor | 560 | 100 Sq.ft | 2453.02 | 13736.912
| c) Second Floor | 60 | 100 Sq.ft | 2531.07 | 1518.642
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 40 | 100 Sq.ft | 3075.7 | 1230.28
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor. | 4500 | 100 Sq.ft. | 560.9844 | 25244.2969
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 60 | Sft. | 571.6761 | 34300.5651
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required .... | 0 | Sft. | 551.814 | 0
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 0 | Sq ft | 303.1167 | 0
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required. | 25 | Sq ft | 503.6173 | 12590.4319
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required. | 60 | Sq ft | 419.1321 | 25147.9286
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 0 | Sq ft | 91.9382 | 0
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required. | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required. | 50 | Sft | 327.3112 | 16365.5619
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 4500 | 100 Sq.ft. | 505.095 | 22729.275
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 1650 | 100 Sq.ft | 789.1413 | 13020.8306
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 1250 | 100 Sq.ft. | 751.51 | 9393.875
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 60 | 100 Sft. | 415.4358 | 249.2615
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | 85 | Sft | 494.9753 | 42072.9019
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 330.2261 | 19813.5648
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sft | 629.3167 | 37759.002
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 0 | Sq.ft. | 447.0099 | 0
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 60 | Sq.ft. | 106.1059 | 6366.3514
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 460 | 100 Sq.ft. | 3053.2494 | 14044.9473
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 1500 | 100 Sqft | 17882.3933 | 268235.8988
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 200 | 100 Rft. | 1368.1642 | 2736.3283
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 650 | 100 Sq.ft. | 924.3325 | 6008.1613
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1250 | 100 Sq.ft. | 955.7145 | 11946.4312
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 4000 | 100 Sq.ft. | 124.434 | 4977.36
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 1250 | Sq.ft. | 103.0965 | 128870.625
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor. | 0 | Sqft | 363.11 | 0
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 5 | Cwt | 9607.9425 | 48039.7123
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 20 | 100 Sq.ft | 12123.2262 | 2424.6452
| b) First Floor | 25 | 100 Sq.ft | 12365.19 | 3091.2975
| c) Second Floor | 25 | 100 Sq.ft | 12653.98 | 3163.495
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 650 | 100 Sq.ft | 8408.2262 | 54653.47
| b) First Floor | 850 | 100 Sq.ft | 8650.19 | 73526.615
| c) Second Floor | 40 | 100 Sq.ft | 8938.98 | 3575.592
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 4 | Cwt. | 7634.0786 | 30536.3145
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 4 | Each | 2531.555 | 10126.22
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 4000 | 100 Sq.ft. | 602.78 | 24111.2
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 25 | Each | 1063.8056 | 26595.14
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 0 | Each | 2420.5025 | 0
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size. | 3 | Each | 407.2754 | 1221.8261
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent. | 4000 | 100 Sq.ft. | 2659.7875 | 106391.4983
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 60 | Ib | 145.396 | 8723.76
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 80 | Rft. | 210.5485 | 16843.8833
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 6 | Each | 159.1642 | 954.9852
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 6 | Each | 629.85 | 3779.1
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 0 | % Cft | 42.3057 | 0
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 0 | 100 Sq.ft. | 1878.9641 | 0
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 300 | Rft. | 9.6687 | 2900.625
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 0 | lbs | 76.49 | 0
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 0 | cwt | 7997.6 | 0
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 0 | rft | 333.08 | 0
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 0 | Sqft | 678.32 | 0
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 0 | Sq. In | 0.95 | 0
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 150 | 100 Sq.ft | 135.06 | 202.59
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 150 | 100 Sq.ft | 284.54 | 426.81
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 250 | 100 Sq.ft | 2371.9061 | 5929.7651
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 250 | 100 Sft | 727.47 | 1818.675
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 0 | Sft | 71.69 | 0
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 650 | 100 Sft. | 9097.3098 | 59132.5134
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 50 | 100 Sq.ft | 43.4293 | 21.7146
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 500 | 100 Sq.ft | 110.385 | 551.925
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 5 | cwt | 5988.48 | 29942.4
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 10000 | 100 Sq.ft. | 139.9325 | 13993.25
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 60 | SQFT | 48.02 | 2881.2
| TOTAL OF SUB -HEAD A |  |  |  | 2542229.5728
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (DOCTOR'S RESIDENCE )
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired. | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 1400 | 100 Cft | 2823.86 | 39534.04
| TOTAL OF SUB HEAD B |  |  |  | 39534.04
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (DOCTOR'S RESIDENCE )
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4. | 4 | Each | 3424.916 | 13699.664
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 4 | Each | 4601.3 | 18405.2
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4. | 4 | Each | 4628.14 | 18512.56
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal. | 4 | Each | 863.83 | 3455.32
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 10 | Each | 389.752 | 3897.52
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 4 | Each | 968.44 | 3873.76
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 6 | Each | 534.3008 | 3205.8048
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 8 | Each | 595.3024 | 4762.4192
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 15 | Each | 279.75 | 4196.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 0 | Each | 66891 | 0
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 20 | Rft | 68.32 | 1366.4
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 25 | Rft | 85.26 | 2131.5
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 20 | Rft | 120.35 | 2407
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 20 | Rft | 158.07 | 3161.4
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 125 | Rft | 35.21 | 4401.25
| Do. Do. 1 inch (25mm) dia. | 25 | Rft | 42.23 | 1055.75
| Do. Do. 1-1/4 inch (32 mm) dia.. | 25 | Rft | 64.23 | 1605.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 50 | Rft | 82.1 | 4105
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 50 | R.ft | 67.8153 | 3390.7632
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 25 | R.ft | 88.2753 | 2206.8816
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 20 | R.ft | 127.734 | 2554.6805
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 20 | Each | 882.9832 | 17659.664
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 6 | Each | 17442.4785 | 104654.8708
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m). | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe. | 250 | R.ft. | 250.26 | 62565
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 6 | Each | 1500 | 9000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 6 | Each | 105 | 630
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 5 | Each | 215 | 1075
| PPRC Ball Valve 20 mm. | 5 | Each | 643.5 | 3217.5
| PPRC Ball Valve 25 mm. | 2 | Each | 783.75 | 1567.5
| TOTAL OF SUB HEAD C |  |  |  | 437125.3425
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (DOCTOR'S RESIDENCE )
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 450 | Rft | 25 | 11250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 550 | 100 Sq.ft. | 12000 | 66000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 0 | Sft | 700 | 0
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 180 | Rft | 140 | 25200
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 180 | Rft | 225 | 40500
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 25 | R.ft | 200.08 | 5002
| 8 inch dia | 30 | R.ft | 352.16 | 10564.8
| 12 inch dia | 40 | R.ft | 719.35 | 28774
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| b) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 33250 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 75 | Rft | 310 | 23250
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total Of Non Schedule Items |  |  |  | 307040.8
SUMMARY
| Total of Sub Head 'A' | 2542229.5728
| Total of Sub Head 'B' | 39534.04
| Total of Sub Head 'C' | 437125.3425
| Total of Non-Schedule Items | 307040.8
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 3325929.7553

## Kotri Para Med Res
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (PARA MEDICAL STAFF RESIDENCE )
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 8 | Each | 197.795 | 1582.36
| b) First Floor | 6 | Each | 211.61 | 1269.66
| c) Second Floor | 0 | Each | 225.42 | 0
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 8 | Each | 127.075 | 1016.6
| b) First Floor | 6 | Each | 137.58 | 825.48
| c) Second Floor | 0 | Each | 148.08 | 0
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 18 | Cft. | 4595.1353 | 82712.4352
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 10 | 100 Cft. | 2773.55 | 277.355
| b) First Floor | 20 | 100 Cft. | 3024.39 | 604.878
| c) Second Floor | 25 | 100 Cft. | 3253.68 | 813.42
| d) Third Floor | 0 | 100 Cft. | 3482.97 | 0
9/123 | Dismantling burnt brick masonry in lime or cement mortar foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed within three chains (91.5 m). | 80 | 100 Cft. | 988.975 | 791.18
| b) First Floor | 350 | 100 Cft. | 1103.9 | 3863.65
| c) Second Floor | 120 | 100 Cft. | 1385.51 | 1662.612
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 0 | 100 Cft. | 988.975 | 0
| b) First Floor | 0 | 100 Cft. | 1239.82 | 0
| c) Second Floor | 0 | 100 Cft. | 1469.11 | 0
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 150 | 100 Cft | 535.0885 | 802.6327
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 20 | 100 Cft | 10085.8049 | 2017.161
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 25 | 100 Cft. | 18172.93 | 4543.2325
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 20 | 100 Cft. | 17514.88 | 3502.976
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 20 | 100 Cft. | 22448.44 | 4489.688
| b) First Floor | 20 | 100 Cft. | 23397.64 | 4679.528
| c) Second Floor | 0 | 100 Cft. | 24149.14 | 0
| d) Third Floor | 0 | 100 Cft. | 24900.64 | 0
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 20 | 100 Cft. | 20668.6 | 4133.72
| b) First Floor | 60 | 100 Cft. | 21617.8 | 12970.68
| c) Second Floor | 40 | 100 Cft. | 22369.25 | 8947.7
| d) Third Floor | 0 | 100 Cft. | 23120.7 | 0
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 60 | 100 Cft. | 20143.99 | 12086.394
| b) First Floor | 650 | 100 Cft. | 21093.19 | 137105.735
| c) Second Floor | 260 | 100 Cft. | 21844.64 | 56796.064
| d) Third Floor | 0 | 100 Cft. | 22596.09 | 0
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 10 | 100 Cft. | 22538.92 | 2253.892
| b) First Floor | 40 | 100 Cft. | 23488.12 | 9395.248
| c) Second Floor | 10 | 100 Cft. | 24239.57 | 2423.957
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 0 | 100 Cft. | 25857.43 | 0
24/112 | Providing and laying first class solid burnt brick masonry set in cement mortar 1:6 in straight or curved walls 9 to 13-1/2 inches (229 mm to 343 mm) thick including scaffolding, raking, out joints and curing etc. complete in ground floor superstructure . | 350 | 100 Cft. | 21905.3463 | 76668.712
| b) First Floor | 450 | 100 Cft. | 22096.78 | 99435.51
| c) Second Floor | 250 | 100 Cft. | 22776.26 | 56940.65
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 500 | 100 Cft. | 1730.7392 | 8653.6959
| b) First Floor | 800 | 100 Cft. | 1935.9 | 15487.2
| c) Second Floor | 800 | 100 Cft. | 2066.36 | 16530.88
1/122 | 1/4" (6.4 mm) thick cement plaster 1:3 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 1500 | 100 Cft. | 1710.9844 | 25664.7658
| b) First Floor | 1600 | 100 Cft. | 1864.85 | 29837.6
| c) Second Floor | 450 | 100 Cft. | 2138.58 | 9623.61
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 10 | Cwt. | 6249.9391 | 62499.3906
| b) First Floor | 30 | Cwt. | 6323.42 | 189702.6
| c) Second Floor | 30 | Cwt. | 6396.9 | 191907
| d) Third Floor | 0 | Cwt. | 6470.38 | 0
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 0 | 100 Cft. | 15033.28 | 0
| b) First Floor | 0 | 100 Cft. | 15857.05 | 0
| c) Second Floor | 0 | 100 Cft. | 16536.53 | 0
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 260 | 100 Sq.ft | 2204.0168 | 5730.4436
| b) First Floor | 650 | 100 Sq.ft | 2328.9 | 15137.85
| c) Second Floor | 0 | 100 Sq.ft | 2406.95 | 0
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 450 | 100 Sq.ft | 2328.1361 | 10476.6125
| b) First Floor | 560 | 100 Sq.ft | 2453.02 | 13736.912
| c) Second Floor | 60 | 100 Sq.ft | 2531.07 | 1518.642
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 40 | 100 Sq.ft | 3075.7 | 1230.28
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 6000 | 100 Sq.ft. | 560.9844 | 33659.0625
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 60 | Sft. | 571.6761 | 34300.5651
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 0 | Sft. | 551.814 | 0
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 0 | Sq ft | 303.1167 | 0
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 0 | Sq ft | 503.6173 | 0
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 60 | Sq ft | 419.1321 | 25147.9286
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 0 | Sq ft | 91.9382 | 0
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required. | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 0 | Sft | 327.3112 | 0
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 0 | 100 Sq.ft. | 505.095 | 0
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 0 | 100 Sq.ft | 789.1413 | 0
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 1250 | 100 Sq.ft. | 751.51 | 9393.875
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 60 | 100 Sft. | 415.4358 | 249.2615
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | 285 | Sft | 494.9753 | 141067.9652
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 0 | Sq.ft. | 330.2261 | 0
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 0 | Sft | 629.3167 | 0
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 0 | Sq.ft. | 447.0099 | 0
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 0 | Sq.ft. | 106.1059 | 0
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 1250 | 100 Sq.ft. | 3053.2494 | 38165.6178
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 0 | 100 Sqft | 17882.3933 | 0
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 200 | 100 Rft. | 1368.1642 | 2736.3283
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 650 | 100 Sq.ft. | 924.3325 | 6008.1613
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1250 | 100 Sq.ft. | 955.7145 | 11946.4312
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 4000 | 100 Sq.ft. | 124.434 | 4977.36
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 1250 | Sq.ft. | 103.0965 | 128870.625
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 0 | Sqft | 363.11 | 0
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 5 | Cwt | 9607.9425 | 48039.7123
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 20 | 100 Sq.ft | 12123.2262 | 2424.6452
| b) First Floor | 25 | 100 Sq.ft | 12365.19 | 3091.2975
| c) Second Floor | 25 | 100 Sq.ft | 12653.98 | 3163.495
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 650 | 100 Sq.ft | 8408.2262 | 54653.47
| b) First Floor | 850 | 100 Sq.ft | 8650.19 | 73526.615
| c) Second Floor | 40 | 100 Sq.ft | 8938.98 | 3575.592
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 4 | Cwt. | 7634.0786 | 30536.3145
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 4 | Each | 2531.555 | 10126.22
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 4000 | 100 Sq.ft. | 602.78 | 24111.2
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 25 | Each | 1063.8056 | 26595.14
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 0 | Each | 2420.5025 | 0
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 3 | Each | 407.2754 | 1221.8261
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 4000 | 100 Sq.ft. | 2659.7875 | 106391.4983
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 60 | Ib | 145.396 | 8723.76
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 80 | Rft. | 210.5485 | 16843.8833
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 6 | Each | 159.1642 | 954.9852
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 6 | Each | 629.85 | 3779.1
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 0 | % Cft | 42.3057 | 0
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 0 | 100 Sq.ft. | 1878.9641 | 0
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 300 | Rft. | 9.6687 | 2900.625
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 0 | lbs | 76.49 | 0
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 0 | cwt | 7997.6 | 0
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 0 | rft | 333.08 | 0
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 0 | Sqft | 678.32 | 0
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 0 | Sq. In | 0.95 | 0
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 150 | 100 Sq.ft | 135.06 | 202.59
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 150 | 100 Sq.ft | 284.54 | 426.81
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 250 | 100 Sq.ft | 2371.9061 | 5929.7651
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 250 | 100 Sft | 727.47 | 1818.675
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 0 | Sft | 71.69 | 0
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 650 | 100 Sft. | 9097.3098 | 59132.5134
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 50 | 100 Sq.ft | 43.4293 | 21.7146
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 500 | 100 Sq.ft | 110.385 | 551.925
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 5 | cwt | 5988.48 | 29942.4
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 10000 | 100 Sq.ft. | 139.9325 | 13993.25
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required. | 60 | SQFT | 48.02 | 2881.2
| TOTAL OF SUB -HEAD A |  |  |  | 2280394.587
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (PARA MEDICAL STAFF RESIDENCE )
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired. | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 1400 | 100 Cft | 2823.86 | 39534.04
| TOTAL OF SUB HEAD B |  |  |  | 39534.04
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (PARA MEDICAL STAFF RESIDENCE )
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4. | 8 | Each | 3424.916 | 27399.328
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 0 | Each | 4601.3 | 0
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4. | 8 | Each | 4628.14 | 37025.12
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal. | 8 | Each | 863.83 | 6910.64
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 10 | Each | 389.752 | 3897.52
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 4 | Each | 968.44 | 3873.76
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 0 | Each | 534.3008 | 0
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 8 | Each | 595.3024 | 4762.4192
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 0 | Each | 720.94 | 0
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 15 | Each | 279.75 | 4196.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 20 | Rft | 68.32 | 1366.4
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 25 | Rft | 85.26 | 2131.5
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 20 | Rft | 120.35 | 2407
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 20 | Rft | 158.07 | 3161.4
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 125 | Rft | 35.21 | 4401.25
| Do. Do. 1 inch (25mm) dia. | 25 | Rft | 42.23 | 1055.75
| Do. Do. 1-1/4 inch (32 mm) dia.. | 25 | Rft | 64.23 | 1605.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 50 | Rft | 82.1 | 4105
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 50 | R.ft | 67.8153 | 3390.7632
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 25 | R.ft | 88.2753 | 2206.8816
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 20 | R.ft | 127.734 | 2554.6805
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 20 | Each | 882.9832 | 17659.664
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 6 | Each | 17442.4785 | 104654.8708
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe.. | 250 | R.ft. | 250.26 | 62565
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 6 | Each | 1500 | 9000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 6 | Each | 105 | 630
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 5 | Each | 215 | 1075
| PPRC Ball Valve 20 mm. | 5 | Each | 643.5 | 3217.5
| PPRC Ball Valve 25 mm. | 2 | Each | 783.75 | 1567.5
| TOTAL OF SUB HEAD C |  |  |  | 510863.4817
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (PARA MEDICAL STAFF RESIDENCE )
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 450 | Rft | 25 | 11250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 550 | 100 Sq.ft. | 12000 | 66000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 0 | Sft | 700 | 0
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 180 | Rft | 140 | 25200
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 180 | Rft | 225 | 40500
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 25 | R.ft | 200.08 | 5002
| 8 inch dia | 30 | R.ft | 352.16 | 10564.8
| 12 inch dia | 40 | R.ft | 719.35 | 28774
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 33250 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 75 | Rft | 310 | 23250
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total Of Non Schedule Items |  |  |  | 307040.8
SUMMARY
| Total of Sub Head 'A' | 2280394.587
| Total of Sub Head 'B' | 39534.04
| Total of Sub Head 'C' | 510863.4817
| Total of Non-Schedule Items | 307040.8
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 3137832.9088

## Kotri Despensary New
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI DESPENSARY AND ADDITION OF NEW BLOCK AT KOTRI
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 12 | Each | 197.795 | 2373.54
| b) First Floor | 4 | Each | 211.61 | 846.44
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 4 | Each | 127.075 | 508.3
| b) First Floor | 0 | Each | 137.58 | 0
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 60 | Cft. | 4595.1353 | 275708.1175
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 20 | 100 Cft. | 2773.55 | 554.71
| b) First Floor | 40 | 100 Cft. | 3024.39 | 1209.756
9/123 | Dismantling burnt brick masonry in lime or cement mortar foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed within three chains (91.5 m).. | 50 | 100 Cft. | 988.975 | 494.4875
| b) First Floor | 25 | 100 Cft. | 1103.9 | 275.975
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 7500 | 100 Cft | 535.0885 | 40131.6375
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 450 | 100 Cft | 10085.8049 | 45386.122
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 445.5 | 100 Cft. | 18172.93 | 80960.4031
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 550 | 100 Cft. | 17514.88 | 96331.84
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 375 | 100 Cft. | 22448.44 | 84181.65
| b) First Floor | 300 | 100 Cft. | 23397.64 | 70192.92
| c) Second Floor | 125 | 100 Cft. | 24149.14 | 30186.425
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 550 | 100 Cft. | 20668.6 | 113677.3
| b) First Floor | 550 | 100 Cft. | 21617.8 | 118897.9
| c) Second Floor | 250 | 100 Cft. | 22369.25 | 55923.125
56/114 | Providing and Laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 3250 | 100 Cft. | 20143.99 | 654679.675
| b) First Floor | 3100 | 100 Cft. | 21093.19 | 653888.89
| c) Second Floor | 750 | 100 Cft. | 21844.64 | 163834.8
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | 475 | 100 Cft. | 22538.92 | 107059.87
| b) First Floor | 650 | 100 Cft. | 23488.12 | 152672.78
| c) Second Floor | 40 | 100 Cft. | 24239.57 | 9695.828
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 350 | 100 Cft. | 25857.43 | 90501.005
24/112 | Providing and laying first class solid burnt brick masonry set in cement mortar 1:6 in straight or curved walls 9 to 13-1/2 inches (229 mm to 343 mm) thick including scaffolding, raking, out joints and curing etc. complete in ground floor superstructure. | 6500 | 100 Cft. | 21905.3463 | 1423847.5079
| b) First Floor | 8560 | 100 Cft. | 22096.78 | 1891484.368
| c) Second Floor | 2450 | 100 Cft. | 22776.26 | 558018.37
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 13000 | 100 Cft. | 1730.7392 | 224996.0937
| b) First Floor | 13500 | 100 Cft. | 1935.9 | 261346.5
| c) Second Floor | 2650 | 100 Cft. | 2066.36 | 54758.54
1/122 | 1/4" (6.4 mm) thick cement plaster 1:4 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete. | 3500 | 100 Cft. | 1710.9844 | 59884.4536
| b) First Floor | 3500 | 100 Cft. | 1864.85 | 65269.75
| c) Second Floor | 750 | 100 Cft. | 2138.58 | 16039.35
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension. | 220 | Cwt. | 6249.9391 | 1374986.5931
| b) First Floor | 180 | Cwt. | 6323.42 | 1138215.6
| c) Second Floor | 80 | Cwt. | 6396.9 | 511752
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 1260 | 100 Sq.ft | 2204.0168 | 27770.6113
| b) First Floor | 500 | 100 Sq.ft | 2328.9 | 11644.5
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 850 | 100 Sq.ft | 2328.1361 | 19789.1569
| b) First Floor | 560 | 100 Sq.ft | 2453.02 | 13736.912
| c) Second Floor | 60 | 100 Sq.ft | 2531.07 | 1518.642
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 850 | 100 Sq.ft | 3075.7 | 26143.45
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor. | 12500 | 100 Sq.ft. | 560.9844 | 70123.0469
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 950 | Sft. | 571.6761 | 543092.2803
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 125 | Sft. | 551.814 | 68976.7491
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required. | 450 | Sq ft | 303.1167 | 136402.5312
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 650 | Sq ft | 503.6173 | 327351.2293
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required. | 560 | Sq ft | 419.1321 | 234714.0001
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 675 | Sq ft | 91.9382 | 62058.2651
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required. | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 650 | Rft | 35.6642 | 23181.7154
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required. | 50 | Sft | 327.3112 | 16365.5619
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 9500 | 100 Sq.ft. | 505.095 | 47984.025
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 2650 | 100 Sq.ft | 789.1413 | 20912.2431
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor. | 3650 | 100 Sq.ft. | 751.51 | 27430.115
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 360 | 100 Sft. | 415.4358 | 1495.5689
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | 85 | Sft | 494.9753 | 42072.9019
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 330.2261 | 19813.5648
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 260 | Sft | 629.3167 | 163622.3418
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 447.0099 | 26820.5966
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 550 | Sq.ft. | 106.1059 | 58358.2213
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 460 | 100 Sq.ft. | 3053.2494 | 14044.9473
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 8500 | 100 Sqft | 17882.3933 | 1520003.4268
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 850 | Sft | 74.8883 | 63655.0601
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 350 | 100 Rft. | 1368.1642 | 4788.5746
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 650 | 100 Sq.ft. | 924.3325 | 6008.1613
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1250 | 100 Sq.ft. | 955.7145 | 11946.4312
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 6500 | 100 Sq.ft. | 124.434 | 8088.21
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors. | 1250 | Sq.ft. | 103.0965 | 128870.625
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor. | 250 | Sqft | 363.11 | 90777.4876
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 8 | Cwt | 9607.9425 | 76863.5396
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 50 | 100 Sq.ft | 12123.2262 | 6061.6131
| b) First Floor | 25 | 100 Sq.ft | 12365.19 | 3091.2975
| c) Second Floor | 25 | 100 Sq.ft | 12653.98 | 3163.495
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 650 | 100 Sq.ft | 8408.2262 | 54653.47
| b) First Floor | 850 | 100 Sq.ft | 8650.19 | 73526.615
| c) Second Floor | 85 | 100 Sq.ft | 8938.98 | 7598.133
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 85 | Cwt. | 7634.0786 | 648896.6836
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 40 | Each | 2531.555 | 101262.2
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m). | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 5500 | 100 Sq.ft. | 487.86 | 26832.3
| c) Second Floor | 500 | 100 Sq.ft. | 602.78 | 3013.9
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 25 | Each | 1063.8056 | 26595.14
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm. | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge. | 5 | Each | 2420.5025 | 12102.5125
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size. | 3 | Each | 407.2754 | 1221.8261
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent. | 3500 | 100 Sq.ft. | 2659.7875 | 93092.561
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 250 | Ib | 145.396 | 36349
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete. | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete. | 120 | Rft. | 210.5485 | 25265.825
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe. | 10 | Each | 159.1642 | 1591.642
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete. | 10 | Each | 629.85 | 6298.5
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 6500 | % Cft | 42.3057 | 2749.8714
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor. | 160 | 100 Sq.ft. | 1878.9641 | 3006.3426
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors. | 300 | Rft. | 9.6687 | 2900.625
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.) | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 2 | cwt | 7997.6 | 15995.2
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors. | 25 | rft | 333.08 | 8327
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height. | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete. | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor. | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor. | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 150 | 100 Sq.ft | 135.06 | 202.59
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 150 | 100 Sq.ft | 284.54 | 426.81
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 250 | 100 Sq.ft | 2371.9061 | 5929.7651
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor. | 250 | 100 Sft | 727.47 | 1818.675
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 450 | Sft | 71.69 | 32260.5
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 2650 | 100 Sft. | 9097.3098 | 241078.7085
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 50 | 100 Sq.ft | 43.4293 | 21.7146
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 500 | 100 Sq.ft | 110.385 | 551.925
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete. | 5 | cwt | 5988.48 | 29942.4
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 20000 | 100 Sq.ft. | 139.9325 | 27986.5
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required. | 60 | SQFT | 48.02 | 2881.2
| TOTAL OF SUB -HEAD A |  |  |  | 16023859.7854
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI DESPENSARY AND ADDITION OF NEW BLOCK AT KOTRI
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired. | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 3600 | 100 Cft | 2823.86 | 101658.96
| TOTAL OF SUB HEAD B |  |  |  | 101658.96
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI DESPENSARY AND ADDITION OF NEW BLOCK AT KOTRI
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4. | 10 | Each | 3424.916 | 34249.16
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 8 | Each | 4601.3 | 36810.4
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4. | 8 | Each | 4628.14 | 37025.12
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal. | 8 | Each | 863.83 | 6910.64
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 10 | Each | 389.752 | 3897.52
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 10 | Each | 534.3008 | 5343.008
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 10 | Each | 595.3024 | 5953.024
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 15 | Each | 279.75 | 4196.25
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 40 | Rft | 68.32 | 2732.8
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 45 | Rft | 85.26 | 3836.7
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 30 | Rft | 120.35 | 3610.5
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 20 | Rft | 158.07 | 3161.4
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 25 | Rft | 170.58 | 4264.5
| Do. 2inches (50 mm) dia pipe (ILLM). | 20 | Rft | 232.03 | 4640.6
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 125 | Rft | 35.21 | 4401.25
| Do. Do. 1 inch (25mm) dia. | 135 | Rft | 42.23 | 5701.05
| Do. Do. 1-1/4 inch (32 mm) dia.. | 125 | Rft | 64.23 | 8028.75
| Do. Do. 1-1/2 inch (40 mm) dia.. | 250 | Rft | 82.1 | 20525
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 250 | R.ft | 67.8153 | 16953.816
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 45 | R.ft | 88.2753 | 3972.3869
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 55 | R.ft | 127.734 | 7025.3713
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 20 | Each | 882.9832 | 17659.664
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 10 | Each | 17442.4785 | 174424.7846
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m). | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe. | 250 | R.ft. | 250.26 | 62565
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 10 | Each | 720.94 | 7209.4
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 30 | Cft. | 664.8382 | 19945.146
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 6 | Each | 1500 | 9000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 6 | Each | 105 | 630
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 5 | Each | 125 | 625
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 5 | Each | 215 | 1075
| PPRC Ball Valve 20 mm. | 5 | Each | 643.5 | 3217.5
| PPRC Ball Valve 25 mm. | 2 | Each | 783.75 | 1567.5
| TOTAL OF SUB HEAD C |  |  |  | 690567.7293
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI DESPENSARY AND ADDITION OF NEW BLOCK AT KOTRI
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 650 | Rft | 25 | 16250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 550 | 100 Sq.ft. | 12000 | 66000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 25 | Sft | 700 | 17500
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 450 | Rft | 140 | 63000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 450 | Rft | 225 | 101250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 75 | R.ft | 200.08 | 15006
| 8 inch dia | 50 | R.ft | 352.16 | 17608
| 12 inch dia | 50 | R.ft | 719.35 | 35967.5
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 33250 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 75 | Rft | 310 | 23250
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total Of Non Schedule Items |  |  |  | 452331.5
SUMMARY
| Total of Sub Head 'A' | 16023859.7854
| Total of Sub Head 'B' | 101658.96
| Total of Sub Head 'C' | 690567.7293
| Total of Non-Schedule Items | 452331.5
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 17268417.9747

## Med.Centre at Tando Adam
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI MEDICAL CENTRE AT TANDO ADAM
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 4 | Each | 197.795 | 791.18
| b) First Floor | 0 | Each | 211.61 | 0
| c) Second Floor | 0 | Each | 225.42 | 0
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 4 | Each | 127.075 | 508.3
| b) First Floor | 0 | Each | 137.58 | 0
| c) Second Floor | 0 | Each | 148.08 | 0
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 8 | Cft. | 4595.1353 | 36761.0823
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 20 | 100 Cft. | 2773.55 | 554.71
| b) First Floor | 0 | 100 Cft. | 3024.39 | 0
| c) Second Floor | 0 | 100 Cft. | 3253.68 | 0
| d) Third Floor | 0 | 100 Cft. | 3482.97 | 0
9/123 | Dismantling burnt brick masonry in lime or cement mortar foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed within three chains (91.5 m).. | 50 | 100 Cft. | 988.975 | 494.4875
| b) First Floor | 120 | 100 Cft. | 1103.9 | 1324.68
| c) Second Floor | 0 | 100 Cft. | 1385.51 | 0
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 0 | 100 Cft. | 988.975 | 0
| b) First Floor | 0 | 100 Cft. | 1239.82 | 0
| c) Second Floor | 0 | 100 Cft. | 1469.11 | 0
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 450 | 100 Cft | 535.0885 | 2407.8983
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 40 | 100 Cft | 10085.8049 | 4034.322
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 20 | 100 Cft. | 18172.93 | 3634.586
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 20 | 100 Cft. | 17514.88 | 3502.976
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 20 | 100 Cft. | 22448.44 | 4489.688
| b) First Floor | 60 | 100 Cft. | 23397.64 | 14038.584
| c) Second Floor | 0 | 100 Cft. | 24149.14 | 0
| d) Third Floor | 0 | 100 Cft. | 24900.64 | 0
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 20 | 100 Cft. | 20668.6 | 4133.72
| b) First Floor | 140 | 100 Cft. | 21617.8 | 30264.92
| c) Second Floor | 0 | 100 Cft. | 22369.25 | 0
| d) Third Floor | 0 | 100 Cft. | 23120.7 | 0
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 250 | 100 Cft. | 20143.99 | 50359.975
| b) First Floor | 1200 | 100 Cft. | 21093.19 | 253118.28
| c) Second Floor | 0 | 100 Cft. | 21844.64 | 0
| d) Third Floor | 0 | 100 Cft. | 22596.09 | 0
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 10 | 100 Cft. | 22538.92 | 2253.892
| b) First Floor | 40 | 100 Cft. | 23488.12 | 9395.248
| c) Second Floor | 0 | 100 Cft. | 24239.57 | 0
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 30 | 100 Cft. | 25857.43 | 7757.229
24/112 | Providing and laying first class solid burnt brick masonry set in cement mortar 1:6 in straight or curved walls 9 to 13-1/2 inches (229 mm to 343 mm) thick including scaffolding, raking, out joints and curing etc. complete in ground floor superstructure . | 250 | 100 Cft. | 21905.3463 | 54763.3657
| b) First Floor | 2000 | 100 Cft. | 22096.78 | 441935.6
| c) Second Floor | 0 | 100 Cft. | 22776.26 | 0
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 500 | 100 Cft. | 1730.7392 | 8653.6959
| b) First Floor | 3000 | 100 Cft. | 1935.9 | 58077
| c) Second Floor | 0 | 100 Cft. | 2066.36 | 0
1/122 | 1/4" (6.4 mm) thick cement plaster 1:3 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 500 | 100 Cft. | 1710.9844 | 8554.9219
| b) First Floor | 2500 | 100 Cft. | 1864.85 | 46621.25
| c) Second Floor | 0 | 100 Cft. | 2138.58 | 0
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 10 | Cwt. | 6249.9391 | 62499.3906
| b) First Floor | 60 | Cwt. | 6323.42 | 379405.2
| c) Second Floor | 0 | Cwt. | 6396.9 | 0
| d) Third Floor | 0 | Cwt. | 6470.38 | 0
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 0 | 100 Cft. | 15033.28 | 0
| b) First Floor | 0 | 100 Cft. | 15857.05 | 0
| c) Second Floor | 0 | 100 Cft. | 16536.53 | 0
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 60 | 100 Sq.ft | 2204.0168 | 1322.4101
| b) First Floor | 0 | 100 Sq.ft | 2328.9 | 0
| c) Second Floor | 0 | 100 Sq.ft | 2406.95 | 0
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 150 | 100 Sq.ft | 2328.1361 | 3492.2042
| b) First Floor | 560 | 100 Sq.ft | 2453.02 | 13736.912
| c) Second Floor | 60 | 100 Sq.ft | 2531.07 | 1518.642
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 40 | 100 Sq.ft | 3075.7 | 1230.28
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 6500 | 100 Sq.ft. | 560.9844 | 36463.9844
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 60 | Sft. | 571.6761 | 34300.5651
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 0 | Sft. | 551.814 | 0
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 22 | Sq ft | 303.1167 | 6668.5682
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 22 | Sq ft | 503.6173 | 11079.5801
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 0 | Sq ft | 419.1321 | 0
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 0 | Sq ft | 91.9382 | 0
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 0 | Sft | 327.3112 | 0
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 5000 | 100 Sq.ft. | 505.095 | 25254.75
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 1200 | 100 Sq.ft | 789.1413 | 9469.695
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 1200 | 100 Sq.ft. | 751.51 | 9018.12
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 60 | 100 Sft. | 415.4358 | 249.2615
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor.. | 85 | Sft | 494.9753 | 42072.9019
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 330.2261 | 19813.5648
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 40 | Sft | 629.3167 | 25172.668
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 447.0099 | 26820.5966
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 400 | Sq.ft. | 106.1059 | 42442.3428
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 250 | 100 Sq.ft. | 3053.2494 | 7633.1236
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 1200 | 100 Sqft | 17882.3933 | 214588.7191
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 200 | 100 Rft. | 1368.1642 | 2736.3283
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 650 | 100 Sq.ft. | 924.3325 | 6008.1613
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1250 | 100 Sq.ft. | 955.7145 | 11946.4312
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 4500 | 100 Sq.ft. | 124.434 | 5599.53
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 1250 | Sq.ft. | 103.0965 | 128870.625
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 125 | Sqft | 363.11 | 45388.7438
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 5 | Cwt | 9607.9425 | 48039.7123
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 20 | 100 Sq.ft | 12123.2262 | 2424.6452
| b) First Floor | 10 | 100 Sq.ft | 12365.19 | 1236.519
| c) Second Floor | 0 | 100 Sq.ft | 12653.98 | 0
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 450 | 100 Sq.ft | 8408.2262 | 37837.0177
| b) First Floor | 850 | 100 Sq.ft | 8650.19 | 73526.615
| c) Second Floor | 0 | 100 Sq.ft | 8938.98 | 0
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 4 | Cwt. | 7634.0786 | 30536.3145
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 10 | Each | 2531.555 | 25315.55
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 0 | 100 Sq.ft. | 602.78 | 0
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 25 | Each | 1063.8056 | 26595.14
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 5 | Each | 2420.5025 | 12102.5125
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 3 | Each | 407.2754 | 1221.8261
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 2500 | 100 Sq.ft. | 2659.7875 | 66494.6864
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 150 | Ib | 145.396 | 21809.4
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 120 | Rft. | 210.5485 | 25265.825
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 10 | Each | 159.1642 | 1591.642
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 10 | Each | 629.85 | 6298.5
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 150 | % Cft | 42.3057 | 63.4586
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 0 | 100 Sq.ft. | 1878.9641 | 0
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 300 | Rft. | 9.6687 | 2900.625
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 2 | cwt | 7997.6 | 15995.2
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 25 | rft | 333.08 | 8327
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 150 | 100 Sq.ft | 135.06 | 202.59
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 150 | 100 Sq.ft | 284.54 | 426.81
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 250 | 100 Sq.ft | 2371.9061 | 5929.7651
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 250 | 100 Sft | 727.47 | 1818.675
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 450 | Sft | 71.69 | 32260.5
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 250 | 100 Sft. | 9097.3098 | 22743.2744
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 50 | 100 Sq.ft | 43.4293 | 21.7146
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 500 | 100 Sq.ft | 110.385 | 551.925
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 5 | cwt | 5988.48 | 29942.4
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 3000 | 100 Sq.ft. | 139.9325 | 4197.975
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required . | 20 | SQFT | 48.02 | 960.4
| TOTAL OF SUB -HEAD A |  |  |  | 2914242.2995
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (MAIN HOSPITAL )
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 2600 | 100 Cft | 2823.86 | 73420.36
| TOTAL OF SUB HEAD B |  |  |  | 73420.36
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (MAIN HOSPITAL )
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4.. | 6 | Each | 3424.916 | 20549.496
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4.. | 4 | Each | 4601.3 | 18405.2
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4.. | 6 | Each | 4628.14 | 27768.84
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 6 | Each | 863.83 | 5182.98
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 6 | Each | 389.752 | 2338.512
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 4 | Each | 534.3008 | 2137.2032
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 8 | Each | 595.3024 | 4762.4192
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 6 | Each | 720.94 | 4325.64
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 10 | Each | 279.75 | 2797.5
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 20 | Rft | 68.32 | 1366.4
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 20 | Rft | 85.26 | 1705.2
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 15 | Rft | 120.35 | 1805.25
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 10 | Rft | 158.07 | 1580.7
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 0 | Rft | 170.58 | 0
| Do. 2inches (50 mm) dia pipe (ILLM). | 0 | Rft | 232.03 | 0
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 60 | Rft | 35.21 | 2112.6
| Do. Do. 1 inch (25mm) dia. | 80 | Rft | 42.23 | 3378.4
| Do. Do. 1-1/4 inch (32 mm) dia.. | 80 | Rft | 64.23 | 5138.4
| Do. Do. 1-1/2 inch (40 mm) dia.. | 80 | Rft | 82.1 | 6568
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 120 | R.ft | 67.8153 | 8137.8317
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 45 | R.ft | 88.2753 | 3972.3869
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 25 | R.ft | 127.734 | 3193.3506
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 10 | Each | 882.9832 | 8829.832
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 6 | Each | 17442.4785 | 104654.8708
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe. | 250 | R.ft. | 250.26 | 62565
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 8 | Each | 720.94 | 5767.52
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 20 | Cft. | 664.8382 | 13296.764
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 6 | Each | 1500 | 9000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 4 | Each | 105 | 420
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 3 | Each | 125 | 375
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 2 | Each | 215 | 430
| PPRC Ball Valve 20 mm. | 2 | Each | 643.5 | 1287
| PPRC Ball Valve 25 mm. | 1 | Each | 783.75 | 783.75
| TOTAL OF SUB HEAD C |  |  |  | 496836.1348
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (MAIN HOSPITAL )
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 250 | Rft | 25 | 6250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 50 | 100 Sq.ft. | 12000 | 6000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 0 | Sft | 700 | 0
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 250 | Rft | 140 | 35000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 250 | Rft | 225 | 56250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 50 | R.ft | 200.08 | 10004
| 8 inch dia | 20 | R.ft | 352.16 | 7043.2
| 12 inch dia | 20 | R.ft | 719.35 | 14387
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| Bb) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 33250 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 75 | Rft | 310 | 23250
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total Of Non Schedule Items |  |  |  | 254684.2
SUMMARY
| Total of Sub Head 'A' | 2914242.2995
| Total of Sub Head 'B' | 73420.36
| Total of Sub Head 'C' | 496836.1348
| Total of Non-Schedule Items | 254684.2
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 3739182.9943

## Despensary at Nooriabad
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI DISPENSARY AT NOORIABAD
SUB -HEAD (A ) CIVIL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
SH/Item | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
123/45 | Taking out door and window frames with or without hold fasts in ground floor including cutting walls, stacking salvaged material (serviceable) and disposing of unservice­able material as directed within three chains (91.5 m). | 8 | Each | 197.795 | 1582.36
| b) First Floor | 0 | Each | 211.61 | 0
| c) Second Floor | 0 | Each | 225.42 | 0
123/47 | Taking out carefully shutters of doors and windows in ground floor and stacking as directed within three chains (91.5 m). | 8 | Each | 127.075 | 1016.6
| b) First Floor | 0 | Each | 137.58 | 0
| c) Second Floor | 0 | Each | 148.08 | 0
120/2 | Providing and fixing best quality deodar frames for doors. windows, ventilators, clerestory windows, shelves, partitions, trellis work, etc., as required . | 8 | Cft. | 4595.1353 | 36761.0823
123/15 | Dismantling R.C.C. including separating reinforcement from concrete in foundation, basement, plinth and ground floor including stacking at site and disposing of unserviceable material within three chains (91.5 m) | 20 | 100 Cft. | 2773.55 | 554.71
| b) First Floor | 0 | 100 Cft. | 3024.39 | 0
| c) Second Floor | 0 | 100 Cft. | 3253.68 | 0
| d) Third Floor | 0 | 100 Cft. | 3482.97 | 0
9/123 | Dismantling burnt brick masonry in lime or cement mortar foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed within three chains (91.5 m).. | 0 | 100 Cft. | 988.975 | 0
| b) First Floor | 0 | 100 Cft. | 1103.9 | 0
| c) Second Floor | 0 | 100 Cft. | 1385.51 | 0
123/11 | Dismantling cement concrete block masonry work in lime or cement mortar in foundation, basement, plinth and ground floor including stacking salvaged material (serviceable) and disposing of surplus material as directed with in three chains (91.5 m). | 120 | 100 Cft. | 988.975 | 1186.77
| b) First Floor | 40 | 100 Cft. | 1239.82 | 495.928
| c) Second Floor | 0 | 100 Cft. | 1469.11 | 0
1/103 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 450 | 100 Cft | 535.0885 | 2407.8983
12/105 | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using graded stone ballast 3 inches (76 mm) and down gauge in foundation including levelling, compacting and curing etc. complete. | 40 | 100 Cft | 10085.8049 | 4034.322
8/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs.. per sq inch at 28 days with a mix not leaner than 1:2:4 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | 20 | 100 Cft. | 18172.93 | 3634.586
1/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in column footing of required shape including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | 20 | 100 Cft. | 17514.88 | 3502.976
23/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in the ground floor | 20 | 100 Cft. | 22448.44 | 4489.688
| b) First Floor | 60 | 100 Cft. | 23397.64 | 14038.584
| c) Second Floor | 0 | 100 Cft. | 24149.14 | 0
| d) Third Floor | 0 | 100 Cft. | 24900.64 | 0
38/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight beams, lintels cantilever beams of required shape or section including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | 20 | 100 Cft. | 20668.6 | 4133.72
| b) First Floor | 140 | 100 Cft. | 21617.8 | 30264.92
| c) Second Floor | 0 | 100 Cft. | 22369.25 | 0
| d) Third Floor | 0 | 100 Cft. | 23120.7 | 0
56/114 | Providing and faying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary slab 5 inches (127 mm) to 6 inches (152 mm) thick Including form work and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor | 450 | 100 Cft. | 20143.99 | 90647.955
| b) First Floor | 800 | 100 Cft. | 21093.19 | 168745.52
| c) Second Floor | 0 | 100 Cft. | 21844.64 | 0
| d) Third Floor | 0 | 100 Cft. | 22596.09 | 0
59/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in ordinary cantilevered slab, horizontal sun-shade or chajja tapered or straight average 3 inches (76 mm) to less then 5 inches (127 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor.. | 10 | 100 Cft. | 22538.92 | 2253.892
| b) First Floor | 40 | 100 Cft. | 23488.12 | 9395.248
| c) Second Floor | 0 | 100 Cft. | 24239.57 | 0
60/114 | Providing and laying reinforced cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 3000 ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in straight walls vertical fins etc. 5 inches (127 mm) to 6 inches (152 mm) thick including form work and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in third floor. | 30 | 100 Cft. | 25857.43 | 7757.229
24/112 | Providing and laying first class solid burnt brick masonry set in cement mortar 1:6 in straight or curved walls 9 to 13-1/2 inches (229 mm to 343 mm) thick including scaffolding, raking, out joints and curing etc. complete in ground floor superstructure . | 0 | 100 Cft. | 21905.3463 | 0
| b) First Floor | 0 | 100 Cft. | 22096.78 | 0
| c) Second Floor | 0 | 100 Cft. | 22776.26 | 0
6/122 | 1/2" (13 mm) thick cement plaster 1:6 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, comers, and curing etc., complete. | 500 | 100 Cft. | 1730.7392 | 8653.6959
| b) First Floor | 3000 | 100 Cft. | 1935.9 | 58077
| c) Second Floor | 0 | 100 Cft. | 2066.36 | 0
1/122 | 1/4" (6.4 mm) thick cement plaster 1:3 on soffits of ceiling, cantilever slabs, sides and soffits of beams etc., in basement, mezzanine and ground floor including making edges, corners and curing etc., complete . | 500 | 100 Cft. | 1710.9844 | 8554.9219
| b) First Floor | 2500 | 100 Cft. | 1864.85 | 46621.25
| c) Second Floor | 0 | 100 Cft. | 2138.58 | 0
119/166 | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | 10 | Cwt. | 6249.9391 | 62499.3906
| b) First Floor | 60 | Cwt. | 6323.42 | 379405.2
| c) Second Floor | 0 | Cwt. | 6396.9 | 0
| d) Third Floor | 0 | Cwt. | 6470.38 | 0
110/44+92+100 | Providing and laying 1:3:6 machine made cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in sand cement mortar 1:6 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | 120 | 100 Cft. | 15033.28 | 18039.936
| b) First Floor | 260 | 100 Cft. | 15857.05 | 41228.33
| c) Second Floor | 0 | 100 Cft. | 16536.53 | 0
125/28 | Plastering 1/2" (13 mm) thick in patches in cement and sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 60 | 100 Sq.ft | 2204.0168 | 1322.4101
| b) First Floor | 0 | 100 Sq.ft | 2328.9 | 0
| c) Second Floor | 0 | 100 Sq.ft | 2406.95 | 0
29/125 | Plastering 3/4" (19 mm) thick in patches in cement sand mortar 1:4 including curing and scraping old damaged portion in regular shape and removal of rubbish from the site etc. complete as per direction of Engineer-in-Charge in ground floor. | 150 | 100 Sq.ft | 2328.1361 | 3492.2042
| b) First Floor | 0 | 100 Sq.ft | 2453.02 | 0
| c) Second Floor | 0 | 100 Sq.ft | 2531.07 | 0
122/8 | 3/4'' (19 mm) thick cement plaster 1:4 on walls and columns etc. in 3rd floor water tank including making edges, corners, and curing etc., complete. | 0 | 100 Sq.ft | 3075.7 | 0
125/158 | Distempering two renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 4500 | 100 Sq.ft. | 560.9844 | 25244.2969
120/61-A | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | 160 | Sft. | 571.6761 | 91468.1735
154/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood swing shutters fully panelled with same wood, with iron helical spring hinges etc. as required ..... | 0 | Sft. | 551.814 | 0
185/120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood partition fully glazed with glass panes 24 oz., (7.34 kg/SM.} deodar wood beading with putty packing to glasses etc., as required . | 22 | Sq ft | 303.1167 | 6668.5682
48/120 | Providing and fixing 1-1/2 inches (38 mm) thick best quality deodar wood shutters partly panelled and partly glazed with piain glass panes 24 oz. (7.3 kg/SM), approved iron hinges and tower bolts, deodar wood beading and putty packing to glasses etc., as required... | 22 | Sq ft | 503.6173 | 11079.5801
139 /120 | Providing and fixing 1-1/4 inches (32 mm) thick best quality deodar wood shutters fully fixed with expanded metal 3/4 inch x 2-1/2 inches (19 mm x 64 mm) mesh 12 gauge with approved iron hinges and tower bolts etc., as required.. | 0 | Sq ft | 419.1321 | 0
193/120 | Providing and fixing 3/4" thick Lasani board partition of approved pattern and beading for joint on the existing frame work as per direction of the engineer incharge. | 0 | Sq ft | 91.9382 | 0
239 /120 | Providing and fixing with sunken iron screws over existing base of iron or wood best quality pan wood moulding as hand rails, stud, laths etc., of approved design over 4 and up-to 6 square inches (26 and up to 39 Sqm) in cross section as required . | 56 | Rft | 209.9983 | 11759.9023
278 /120 | Providing and fixing best quality deodar wood projected beading upto one Sq. inch (6.45 Sqm.) in sections and required design fixed around the panels of doors, windows etc., of any description | 350 | Rft | 35.6642 | 12482.4621
218/120 | Providing and fixing 3/4 inch (19 mm) thick best quality deodar wood planking in shelves or almirahs with or without deodar wood battens 1" x 1 -1 /2" (25 mm x 38 mm) fixed in walls with screws and rawal plugs etc., as required . | 0 | Sft | 327.3112 | 0
125/168 | Repainting two coats with weather shield paint of (ICI) Dulux make and shade on plaster surface (External) including cleaning, sand papering the surface as directed by the Engineer-in-charge in any floor. | 2000 | 100 Sq.ft. | 505.095 | 10101.9
166/125 | Repainting two coats with plastic emulsion paint of (ICI) Dulux make and shade to walls and ceiling including cleaning, and sand papering the surface as directed by the Engineer-in-charge in any floor. | 1500 | 100 Sq.ft | 789.1413 | 11837.1187
159/125 | Distempering three renewal coats with vinyle distemper (Paintex ICI Dulux) of approved make and shade to walls and ceiling etc., including scraping cleaning the old surface in any floor . | 1000 | 100 Sq.ft. | 751.51 | 7515.1
175/125 | Repainting one coat with creosote or solignum to wood work etc including cleaning the old surface as directed by the Engineer-in-Charge in any floor. | 60 | 100 Sft. | 415.4358 | 249.2615
152/122 | Snowceming of approved make and shade in two coats well scrubbed into the surface including finishing smooth at any height in any floor. | 0 | 100 Sft. | 890.9965 | 0
25/119 | Providing and fixing fully glazed double leaf hung steel windows and ventilators made to crittal or equivalent standard and of approved sections painted with two coats of red oxide paint including using approved brass section oxidized fitting, iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor.. | 85 | Sft | 494.9753 | 42072.9019
60/119 | Providing and fixing fully glazed Bronz anodized or powder coated aluminium Fixed windows Partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators) deluxe model box section 101.76mm x 44.50mm and 2mm thick including the cost of aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 330.2261 | 19813.5648
78/119 | Providing and fixing doubble glazed Bronz anodized or Powder Coated aluminium Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Executive model section dubble or single glazed 101mm x 37mm and 1.6mm thick including the cost of aluminium netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 40 | Sft | 629.3167 | 25172.668
81 /119 | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 1.6mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | 60 | Sq.ft. | 447.0099 | 26820.5966
120/119 | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | 400 | Sq.ft. | 106.1059 | 42442.3428
117/6 | Providing and laying floors of 2 inches (51 mm) thick 1:2:4 cement concrete using graded screened bajri 3/4 inch (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, and curing etc. complete. | 250 | 100 Sq.ft. | 3053.2494 | 7633.1236
159/117 | Providing and laying light colour, glazed/non skid vitrified porcelean tiles (Polished) not exceeding 1600 Sqcm each, (Pak made) on walls and floors, in any floor, laid with dry bond (stile bond) over a base of 1" thick cement mortar (1:3) including jointing to tiles with joint filler of approved quality as per direction of the Engineer incharge. | 1200 | 100 Sqft | 17882.3933 | 214588.7191
157/117 | Providing and laying in floor C.C. 1:2:4: tuff paver 2-1/2" thick of approved design and colour pattren (average strength 7000 psi) laid on sand cushion filling of joint with sand and warring etc. complete as per direction of Engineer Incharge. (the cost of sand cushion is included) | 0 | Sft | 74.8883 | 0
124/141 | Providing and laying gola 3" x 3" (76 mm x 76 mm) concrete 1:2:4 using graded screened bajri at junction of roof slab and walls and finished with cement plaster 1:4 including curing etc. complete. | 200 | 100 Rft. | 1368.1642 | 2736.3283
162/125 | Repainting two coats with enamel paint (Robialac) of approved make and shade to iron work including scraping and sand papering the surface as directed by the Engineer-in-Charge in any floor. | 650 | 100 Sq.ft. | 924.3325 | 6008.1613
160/125 | Repainting two coats with enamel paint of approved make and shade to wood work including scraping and sand papering the surface as directed by Engineer-in-Charge in any floor. | 1250 | 100 Sq.ft. | 955.7145 | 11946.4312
151/125 | Chalk washing three renewal coats to walls and ceiling etc. including cleaning the old surface in any floor. | 4500 | 100 Sq.ft. | 124.434 | 5599.53
125/214 | Replacing glass panes of 32 oz. per Sft. (4.00 mm) approx. with iron nails and putty including removing broken ones if required in all floors . | 1250 | Sq.ft. | 103.0965 | 128870.625
119/17 | Providing and fixing collapsible steel shutter or gate with vertical channels, flat iron diagonal top and bottom rails with steel rollers of required size, T-iron bottom track rivetting the junctions, including locking arrangements and handles, cutting and making good damages to walls etc. painting two coats of red oxide paint, fixing bottom track with C.C. 1:2:4 complete as required in any floor .. | 125 | Sqft | 363.11 | 45388.7438
119/18 | Providing and fixing steel gate of flat iron sections of approved design with or without M.S. sheet covering including hold fast, with or without rollers and track arrangement including providing wicket shutter of required size with all accessories and locking arrangement complete as per direction of the Engineer-in-Charge. | 5 | Cwt | 9607.9425 | 48039.7123
125/59 | Replacing marble mosaic tiles 8" x 8" x 1/4" (203 mm x 203 mm x 6.4 mm) with 3/8" (9.5 mm) topping of approved design of light shade in white cement in ground floor, setting in cement mortar 1:2 and washing with cement slurry of matching colour in floor, dado and skirting etc. complete including curing finishing, polishing and removing, rubbish from the site. | 20 | 100 Sq.ft | 12123.2262 | 2424.6452
| b) First Floor | 10 | 100 Sq.ft | 12365.19 | 1236.519
| c) Second Floor | 0 | 100 Sq.ft | 12653.98 | 0
125/69 | Replacing 1/4" (6.4 mm) thick coloured glazed tiles 6" x 6" (152 mm x 152 mm) of approved foreign make in floor, dado and skirting etc. in ground floor and setting in cement mortar 1:2 and washing the tiles with cement slurry of matching colour complete including curing, finishing and removal of rubbish from the site. | 450 | 100 Sq.ft | 8408.2262 | 37837.0177
| b) First Floor | 850 | 100 Sq.ft | 8650.19 | 73526.615
| c) Second Floor | 0 | 100 Sq.ft | 8938.98 | 0
119/43 | Providing and fixing M.S. moulded steel door frame of 4" x 2-1/2" (102 mm x 64 mm) manufactured from mild steel sheet of 18 gauge (1.41 mm) conforming to BSS. 1245 having a single rebate size 1-1/2" x 1/2" (38 mm x 13 mm) with provision of 3 Nos. M.S. plate, section 1-1/2" x 1/4" (38 mm x 6 mm), (2 Nos. 6 inch long welded with frame at not less than 10 points and 1 No., 12 inch long welded with frame at not less than 20 points), with holes and threads for fixing steel hinges, fitted with one locking box of same sheet (point welded inside the frame), 6 Nos. 6 inches long flat iron fixing lugs, of 1-1/4" x 3/16" section, treated with special red oxide primer coat all around including cutting holes and filling the cavity with cement concrete 1:2:4 etc. in any floor at any height complete as directed by the Engineer-in-Charge | 35 | Rft | 157.1211 | 5499.2372
119/32 | Providing and fixing iron grills with required section of flat iron as per approved design including welding all sides of the section at the junction, and fixing with sunk iron screws, painting two coats of red oxide paint etc. complete as required in any floor in masonry or concrete work. | 4 | Cwt. | 7634.0786 | 30536.3145
119/76 | Providing and fixing with brass screws Alpha knob set lock of approved design (No. 7000) Japan make, cutting wood to required shape and size with two operating keys as per direction of the Engineer-in-Charge | 10 | Each | 2531.555 | 25315.55
123/21 | Dismantling lime terracing upto 3" (76 mm) average thickness over roof in ground floor and disposing of the material as directed within three chains (91.5 m) . | 0 | 100 Sq.ft. | 372.9375 | 0
| b) First Floor | 0 | 100 Sq.ft. | 487.86 | 0
| c) Second Floor | 0 | 100 Sq.ft. | 602.78 | 0
124 | Providing and fixing approved brass sliding bolts or aldrop bolts 10" x 5/8" (254 mm x 16 mm) size with necessary brass screws and iron bolts and nuts | 25 | Each | 1063.8056 | 26595.14
151 | Providing and fixing approved heavy type oxidised iron safety hasp and staple 5" (127 mm) size with necessary iron screws. | 10 | Each | 88.5392 | 885.3923
175 | Providing and fixing approved heavy type chromium plated iron handles 5" (127 mm) size with necessary screws | 25 | Each | 59.6369 | 1490.9213
109 | Providing and fixing approved brass parliament hinges with brass screws: 5" x 1/4" or 127 mm x 6-4 mm . | 5 | Each | 382.4221 | 1912.1104
108 | Providing and fixing with iron screws approved piano hinges of iron sheet 3/4" (19 mm) wide as per direction of the Engineer-in-Charge. | 25 | Rft. | 121.8152 | 3045.38
70 | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | 5 | Each | 2420.5025 | 12102.5125
101 | Providing and fixing with iron screws approved single action helical iron spring hinges as per direction of the Engineer-in-Charge: 6" (152 mm) size.. | 3 | Each | 407.2754 | 1221.8261
3/108 | Providing and laying 2 inches (51 mm) thick damp proof course with cement concrete 1:2:4 cast in situ using graded screened bajri of 3/4 inch (19 mm) and down gauge mixed with any approved water proofing agent including compacting, curing form work and its removal etc. complete, but excluding the cost of water proofing agent . | 2500 | 100 Sq.ft. | 2659.7875 | 66494.6864
4 | Extra for using water proofing agent cemto in item Nos. 1,2 and 3 (quantity to be used as per manufacturer's specification). | 150 | Ib | 145.396 | 21809.4
41 | Providing and fixing PVC pipe spouts of 2" (50 mm) dia and required length including fixing in cement mortar 1:4 etc- complete . | 5 | Rft. | 107.7375 | 538.6875
64 | Providing and fixing 3" (80 mm) dia polyvinyle chloride rain water (PVC) down pipe with mild steel clamps, bolts and nuts fixed in cement concrete 1:2:4 etc. complete . | 120 | Rft. | 210.5485 | 25265.825
66 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) sockets for rain water down pipe . | 10 | Each | 159.1642 | 1591.642
68 | Providing and fixing 3" (80 mm) dia polyvinyle chloride (PVC) bend of any degree for rain water down pipe with clamps, bolts and nuts in cement concrete 1:2:4 etc. complete.. | 10 | Each | 629.85 | 6298.5
150 | Providing and fixing holdfasts/iron clamps of M.S. round bars of required design and shape with or without welding including the cost of threading and nuts sunk in frames of doors, windows etc. in any floor complete | 10 | Lbs. | 66.0667 | 660.6672
7 | Cutting to a required gradient in all kinds of soil (except rock) and dressing the ground by bulldozers, grader or scraper including disposal of excavated stuff within 3 chains (91.5 Rm) including all lifts as required. | 150 | % Cft | 42.3057 | 63.4586
189 | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | 0 | 100 Sq.ft. | 1878.9641 | 0
168 | Providing and laying 5 mm glass patties (panel strips) upto 1" (25 mm) depth in floor and dado of any description in all floors . | 300 | Rft. | 9.6687 | 2900.625
4/124 | Cutting holes upto 36 square inches (232 Sqm) in R.C.C. or R.B. walls, floors and roofs upto 9" (229 mm) thick making good the holes with cement concrete 1 ;2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor. | 10 | Each | 54.36 | 543.6
6/124 | Cutting holes in walls of all kinds other than R.C.C. or R.B. upto 9" (229 mm) thick etc. making good the same in cement concrete 1:2:4 including finishing, curing etc. and disposal of rubbish from site complete, in any floor holes above 144 square inches (928 Sqm.) upto 6 Sq.tt. (0.56 Sqm.). | 10 | Each | 84.74 | 847.4
13/124 | Providing and fixing clamps of M. S. bars of required dia for fans as per design at the time of casting in reinforced cement concrete slab or beams. | 10 | lbs | 76.49 | 764.9
17/124 | Providing and fixing galvanized iron barbed wire fencing (with four points) to the posts of any description complete with hooks and binding wire etc- if required (cost of posts not included). | 2 | cwt | 7997.6 | 15995.2
94/124 | Providing and fixing plain polyvinyle chloride (PVC) water stops 8" (203 mm) wide in vertical or horizontal expansion joints including cutting and jointing etc. complete in all floors . | 25 | rft | 333.08 | 8327
101/124 | Providing and filling asphalt bitumen mixed with sand @ 90 Lbs. per Cft. (1443 Kg/Cum.) of sand in expansion joints of roof slab etc. | 2 | cft | 1832.57 | 3665.14
103/124 | Providing and fixing 16 oz. (4.89 Kg/ Sqm.) aluminium sheet covering to expansion joints in walls and columns as per approved design including providing clamps and fixing with screws and rawal plugs or wooden gutties including making slotted holes etc. complete. | 95 | Sqft | 678.32 | 64440.4
105/124 | Cutting M. S. bars, bolts, rivets, steel sections etc. of any shape and size at any height . | 1350 | Sq. In | 0.95 | 1282.5
123/124 | Supplying and fixing ladder of flat iron 2-1/2" x 1/4" (64 mm x 6.4 mm) in section and step bars of 5/8" (16 mm) dia at 18" (457 mm) centre to centre including fixing flat iron stays as per approved design and direction of the Engineer-in-Charge complete . | 2 | cwt | 6074.4 | 12148.8
130/124 | Providing and fixing aluminium sheet of 22 gauge (1.15 mm thick) on wooden surface with sunken aluminium screw of required size as per direction of the Engineer-in-Charge. | 25 | Sqft | 225.13 | 5628.25
2/125 | Repairs to cracks to reinforced cement concrete work by grouting with cement gun with cement mortar 1:2 including cutting the chase of required size, finishing, curing including removal of rubbish etc. from site complete as directed by the Engineer-in-Charge, in ground floor . | 250 | 100Rft | 2258.58 | 5646.45
4/125 | Repairs to cracks in cement mortar 1:4 including cutting the chase upto 3/4" (19 mm) depth, finishing, curing including removal of rubbish etc. from site complete in ground floor . | 250 | 100Rft | 1392.7559 | 3481.8898
22/125 | Removing all sorts of varnish and polishes etc. without blow lamp from wooden surface including removal of rubbish etc- from site as directed, in all floors complete. | 150 | 100 Sq.ft | 135.06 | 202.59
24/125 | Removing cement or lime plaster of any thickness from walls and disposing of the rubbish etc. from site as directed | 150 | 100 Sq.ft | 284.54 | 426.81
91/125 | Replacing 2" (51 mm) thick 1:2:4 cement concrete floor in patches complete in ground floor including form work, watering, curing etc. and dismantling the damaged floor in regular shape and removal of rubbish from the site. | 250 | 100 Sq.ft | 2371.9061 | 5929.7651
107/125 | Replacing expanded metal 3/4" x 2-1/2" (19 mm x 64 mm) mesh 12 gauge (2.1 mm) of approved quality including replacing the beading where necessary wrth best quality imported teak wood of existing design and section with iron screws including dismantling expanded metal and removal of rubbish. | 350 | Sft | 96.8 | 33880
193/125 | Varnishing two renewal coats of approved make to wood work including cleaning the old surface as directed the Engineer-in-Charge in any floor . | 250 | 100 Sft | 727.47 | 1818.675
228/125 | Easing doors, windows and ventilators in all floors. | 275 | Each | 43.1 | 11852.5
229/125 | Cleaning glass panes including removing stains etc. in all floors. | 325 | Sft | 8.84 | 2873
182/124 | Providing and fixing Gypsum board 2' x 2'x 12mm tiles ceiling including Aluminum T & L angle 1" x 1" i.c hanger clips jointing clips and G.I Wire etc complete as required in any floor. | 450 | Sft | 71.69 | 32260.5
176/124 | Providing and fixing aluminium (ribbed) nosing to treads of required sections with aluminium lugs fixed with aluminium screws and rawl plugs etc. as per instructions of the Engineer-in-Charge in all floors | 0 | lbs | 180.48 | 0
127/125 | Providing and fixing 1/4"(6mm approx.) thick of Pakistani make first grade white glazed tiles 8"x 10" (203mm x 254mm) size in dado and skirting in ground floor over 1/2" (13mm) thick base of cement mortar 1:3 setting of tiles in slurry of grey cement over mortar base including filling the joint with white cement and washing the tile, curing and cleaning etc. complete. | 250 | 100 Sft. | 9097.3098 | 22743.2744
48/118 | Clearing jungle (ordinary) by cutting, removing all shrubs, trees, upto 6 inches (152 mm) girth, etc. and taking out their entire roots and filling the hollows with earth complete with dressing, consolidating and watering the filling including stacking the serviceable materials and disposal of useless material as directed, lead to 10 chains (305 Rm), cost of earth included. | 50 | 100 Sq.ft | 43.4293 | 21.7146
1/102 | Levelling and dressing the ground by cutting and filling earth upto 6 inches (152 mm) in depth including consolidating and watering, complete as required. | 500 | 100 Sq.ft | 110.385 | 551.925
3/124 | Providing and fixing angle iron fencing posts embedded in concrete and painting exposed portion with aluminium paint 3 coats including necessary holes but excluding the cost of excavation and concrete, complete . | 5 | cwt | 5988.48 | 29942.4
11/125 | Rubbing and polishing old mosaic floor, dado and skirting in any floors. | 3000 | 100 Sq.ft. | 139.9325 | 4197.975
106/125 | Replacing G.I. wire gauze of 22 gauge and 144 mesh per Sq.inch including replacing the beading where necessary with best quality deodar wood of existing design and section with iron screw including dismantling wire gauze etc. and removal of rubbish as required. | 20 | SQFT | 48.02 | 960.4
| TOTAL OF SUB -HEAD A |  |  |  | 2449063.471
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI DISPENSARY AT NOORIABAD
SUB -HEAD (B ) ROAD WORKS
Schedule Item based on Pak PWD Schedule of Rates 2012
131/127 | Removing the existing worn out bituminous surface, having pot holes and ruts in patches of regular shape brushing and re-carpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specifications complete, including disposal of excavated stuff within one chain (30.5 m) lead as desired . | 0 | 100 Sq.ft. | 3840.8809 | 0
145/127 | Cutting trenches through bituminous road for laying pipes etc. in any width and upto required depth including dismantling kerb stones, edge stones or channels, replacing soling stones (oid and new 10%) with hand refilling with (old and new 25%) ballast blinded with murum, watering and ramming complete, refixing edge stone, kerb stones or channels in cement mortar 1:3 as directed including recarpeting with 1" (25 mm) thick (consolidated) asphalt macadam as per specification complete (cost of new stone, ballast and new murum is inclusive): 3" (76 mm) thick consolidated asphalt macadam recarpet. | 0 | 100 Sq ft | 12266.26 | 0
79/127 | Providing and laying 4" (102 mm) thick not leaner than 1:2:4 cement concrete (minimum works cube crushing strength of 2250 Lbs. PSI (158 Kg. per Sq.cm. at 28 days) in road, paths, crete-ways etc. using graded screened bajri in panels of approved size laid to required gradient and camber over any sub-grade including cost of necessary form work and its removal, compacting with vibrators (immersion or screen or both) belting the surface with canvas belt, roughening the surface after laying concrete with brush and curing etc. complete.. | 0 | 100 Sqft | 6102.5179 | 0
115/127 | Providing and laying road kerb of precast cement concrete 1:2:4 (24" long 6" wide and 12" deep (610 mm long 152 mm wide and 305 mm deep) using screened graded bajri, from work and its removal compacting and curing laid in cement mortar 1:4 and cement plaster 1:4 neatly finished including cost of excavation and back filling of excavated stuff and its disposal within one chain lead as desired. | 0 | 100 Rft. | 13968.6715 | 0
15/102 | Removing old debris and rubbish of all kinds and sizes within a lead of 1 Km including all lifts. | 2600 | 100 Cft | 2823.86 | 73420.36
| TOTAL OF SUB HEAD B |  |  |  | 73420.36
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI DISPENSARY AT NOORIABAD
SUB -HEAD (C ) SANITARY & WATER SUPPLY
Schedule Item based on Pak PWD Schedule of Rates 2012
1/301 | Providing and fixing squatting type W.C.Pan in white vitreous china with integral treads (Pakistani) orissa pattern and C.I. trap 100mm dia. Complete with and including the cost of 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C. flushing pipe suitable for this type with fittings and making requisite number of holes in walls, plinth & floor for pipe connections and making good in cement concrete 1:2:4.. | 6 | Each | 3424.916 | 20549.496
5/301 | Providing and fixing Pakistani best quality European style white glazed earthenware W.,C pan complete with and including the cost of plastic seat and buffers, 13.6 litres best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4.. | 4 | Each | 4601.3 | 18405.2
9/301 | Providing and fixing 22 inches x 16 inches (560 x 406 mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into walls 1/2 inches (15 mm) dia. Chrome plated mixer, 1-1/4 inches (32 mm) rubber plug and chrome plated brass chain 1-1/4 inches (32 mm) dia brass waste of approved pattern 1-1/4 inches (32 mm) dia chromium plated battal trap with unions and making requisite, number of holes in walls, plinth and floor for pip.e connections and making good in cement concrete 1:2:4.. | 6 | Each | 4628.14 | 27768.84
10/301 | Extra over item No. 8 and 9 for providing and fixing best available (Pakistani make) white glazed earthenware pedestal.. | 6 | Each | 863.83 | 5182.98
33/301 | Providing and fixing approved quality stainless steel sink 33” x 18” Pak made (Atlas) complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | 4 | Each | 12406.768 | 49627.072
1/307 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | 6 | Each | 389.752 | 2338.512
25/301 | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | 5 | Each | 6611.132 | 33055.66
2/302 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | 5 | Each | 968.44 | 4842.2
4/302 | Providing and fixing plastic (PVC) toilet paper holder in wall complete of any colour. | 4 | Each | 534.3008 | 2137.2032
5/302 | Providing and fixing 24 inches x 18 inches (610 mm x 457 mm) looking mirror of Imported glass 5 mm thick fixing with CP clamps and screws | 8 | Each | 595.3024 | 4762.4192
13/302 | Providing & fixing chromium plated Muslim bib-cock with out Muslim Shower of approved quality. | 6 | Each | 720.94 | 4325.64
3/307 | Providing & fixing CP 1/2 inches (15 mm) dia brass stop cocks. | 10 | Each | 279.75 | 2797.5
25/307 | Making connection with the existing G.I. pipe upto 2 inches (50 mm) dia including cutting the pipe and providing and fixing necessary fittings. | 10 | Each | 448.58 | 4485.8
31/307 | Providing and fixing water tank made of food grade polyethylene material 1500 gallon (Supper tuff) i/c cost of specials and cartage upto site as per direction of Engineer in charge. | 1 | Each | 66891 | 66891
1/306 | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). 1/2 inch (15 mm) dia pipe. | 20 | Rft | 68.32 | 1366.4
| Do. Do. 3/4 inch (20 mm) dia pipe (ILLM). | 20 | Rft | 85.26 | 1705.2
| Do. Do. 1 inch (25 mm) dia pipe (ILLM). | 15 | Rft | 120.35 | 1805.25
| Do. 1-1/4 inches (32 mm) dia pipe (ILLM). | 10 | Rft | 158.07 | 1580.7
| Do. 1-1/2 inches (40 mm) dia pipe (ILLM). | 0 | Rft | 170.58 | 0
| Do. 2inches (50 mm) dia pipe (ILLM). | 0 | Rft | 232.03 | 0
11/306 | Providing and fixing un platisized polyvinyl chloride pipe (u.P.V.C) "E" class with specials) and clamps etc., including cutting and fitting, complete with and including the cost of breaking through walls and roof and making good etc.; after cleaning the pipe and cartage within 10 miles (16.09 km) (working pressure 12 kg/cm2): 3/4 inch (20 mm) dia. | 60 | Rft | 35.21 | 2112.6
| Do. Do. 1 inch (25mm) dia. | 80 | Rft | 42.23 | 3378.4
| Do. Do. 1-1/4 inch (32 mm) dia.. | 80 | Rft | 64.23 | 5138.4
| Do. Do. 1-1/2 inch (40 mm) dia.. | 80 | Rft | 82.1 | 6568
Do. Do. 2 inches (50 mm) dia pipe..
1/307 | Providing PPRC. pipes, specials and clamps etc., including fixing cutting and fitting complete with and including the cost of breaking through walls and roof, making good etc., and testing with water to a pressure head of 200 feet (61 M) and cartages within 10 miles (16.09 km.) 1/2 inch (15mm) dia pipe. | 120 | R.ft | 67.8153 | 8137.8317
305/1 | Do. Do. 3/4 inch (20 mm) dia pipe. | 45 | R.ft | 88.2753 | 3972.3869
305/2 | Do. Do. 1 inch (25 mm) dia pipe | 25 | R.ft | 127.734 | 3193.3506
305/3 | Providing and fixing 6 inches x 2 inches or 6 inches x 3 inches (150 mm x 50 mm or 150 mm x 80 mm ) C.I. floor trap of approved self cleansing design with C.I. screwed down grating with or without a vent arm complete with and including making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | 10 | Each | 882.9832 | 8829.832
301/15 | Providing manhole type 'B' size 3 feet x 2-1/2 feet or 914 mm x 762 mm (inside dimensions) x 4 feet (1.22m) deep as per approved design and specifications complete 4 inches to 12 inches (100 mm to 305 mm) dia. pipes 4 feet to 7 feet-5 inches (1.22 m to 2.26 m) depth with cast iron cover and frame 18 inches (460 mm) dia. (inside) weight -1 Cwt. 3 Qtrs. (88.90 kg,) in 6 inches (150 mm) thick RCC 1:2:4 slab, 8 inches (203 mm) thick c.c. 1:3:6 block masonry walls set in 1:3 c.m. 6 inches (150mm) thick, 1:3:6, c.c in foundation 1:2:4 c.c in benching, 1/2 inch (13mm) thick cement plaster in 1:4 c.m. to all inside wall surfaces, channels and benching etc. and to top including providing and fixing cast iron foot rest at every foot of depth and making requisite number of main and branch channels complete but excluding the cost of excavation, back filing, disposal of excavated stuff manhole cover and frame. | 6 | Each | 17442.4785 | 104654.8708
315/3 | Excavation in all kinds of soil, murum, hard, average or soft including lift up to 5 feet (1.52 m) and lead up to one chain (30.48 m).. | 550 | %Cft | 599.7012 | 3298.3565
313/5 | Providing R.C.C. pipes and collars of class 'B' and fixing in trench including cutting, fitting and jointing with maxphalt composition and cement mortar (1:1) and back filling the excavated material in trench including testing with water to a pressure head of 50 feet (15.24m) and cartage within 10 miles (16.09 km), for 9 inches (225 mm)dia. pipe.. | 250 | R.ft. | 250.26 | 62565
10 | Providing & fixing chromium plated Muslim Shower of approved quality. | 8 | Each | 720.94 | 5767.52
13 | Providing & laying R.C.C 1:2:4 slab cover 3" thick average (precost complete with M.S flat iron, M.S bars embedded in concrete) of any shape including the cost of reinforcement and welding etc. as per direction of Engineer Incharge. | 20 | Cft. | 664.8382 | 13296.764
29 | Providing and fixing C.P. Mixer Tap 1/2 inch dia for sink. | 6 | Each | 1500 | 9000
| P.V.C. Ball Valve, 1/2 inch (15mm) dia. | 4 | Each | 105 | 420
| P.V.C. Ball Valve, 3/4 inches (20mm) dia. | 3 | Each | 125 | 375
| P.V.C, Ball Valve, 1 inch (25.0mm) dia. | 2 | Each | 215 | 430
| PPRC Ball Valve 20 mm. | 2 | Each | 643.5 | 1287
| PPRC Ball Valve 25 mm. | 1 | Each | 783.75 | 783.75
| TOTAL OF SUB HEAD C |  |  |  | 496836.1348
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI DISPENSARY AT NOORIABAD
Non- Schedule Item based on Prevailing Market Rates
| Providing and fixing floor mounted hinges for glass & almunim doors at all floors complete as per direction of Engineer in Charge | 2 | Each | 4500 | 9000
| Removal of old demaged C.I & G.I worn out pipes as per direction of Engineer in Charge | 250 | Rft | 25 | 6250
| Providing and laying floor of 10mm (approx: 1/2") thick coloured glazed tiles 10" x 5" of National make Pakistani first grade in Floor laid over 1" thick cement mortar 1:2 ( 1 cement and 2 sand) inluding jointing and washing the tiles with grey cement slury and curing etc. complete. | 50 | 100 Sq.ft. | 12000 | 6000
| Providing and fixing toughened glass partition 12mm thick includung all necessary fittings and handle with locking arrangement as per direction of Engineer in charge. | 0 | Sft | 700 | 0
| Providing and fixing 75 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 250 | Rft | 140 | 35000
| Providing and fixing 100 MM dia uPVC pipe class A for soil waste & vent lines pipe conformation to BSS-416 with rubber rings including all specials like plain or plug bends, tees,junctions, collars, cowels, and clamp as required at site and as directed including cutting and fitting in position, cutting holes in floors and walls and making good in all respect. (Dadex or equivalent) | 250 | Rft | 225 | 56250
| Providing and fixing un platisized polyvinyl chloride pipe (uP.V.C) "B" class and specials etc. including cutting and fitting complete with and including the cost of cutting trench upto 1-1/2 feet deep refilling, watering, ramming, and disposal of surplus earth within one chain and after cleaning the pipe and cartage within 10 miles (16.09 km.) (working pressure 10 kg/cm2 ) 6 inches dia. | 50 | R.ft | 200.08 | 10004
| 8 inch dia | 20 | R.ft | 352.16 | 7043.2
| 12 inch dia | 20 | R.ft | 719.35 | 14387
| Termite Proofing: Providing Treatment Proofing Treatment in foundation, column trenches & floor by means of spraying with pressure of under 150 psi with antitermite solution approved chemical as per manufacturer / plant protection specification as directed by the Engineer-in-chrge. (Analyzed Rate) | 0 | Sft | 10 | 0
FIRE FIGHTING
Portable fire extinguishers of following type
| a) Dry chemical powder 6 Kg | 0 | No | 4500 | 0
| b) Carbon dioxide 5 Kg | 0 | No. | 5000 | 0
| c) Foam 9 litre | 0 | No. | 8000 | 0
| Fire Hose Cabinet as per direction of Engineer in charge with all accessories | 0 | No. | 33250 | 0
GAS WORK
| Supply, installation, testing and commisioning of Galvanized Steel pipes, medium grade conforming to BS 1387 with all fittings sockets, bends tees, elbows where required) fixed to walls, ceilings and floor etc. including caps and plugs as per specification and as per direction of Engineer in Charge. 3/4" dia | 150 | Rft | 550 | 82500
| b) 1/2 " dia | 75 | Rft | 310 | 23250
| Providing and fixing ball valves in gas pipe as per specification and direction of Engineer in Charge.1/2" dia | 2 | No | 2500 | 5000
| Total Of Non Schedule Items |  |  |  | 254684.2
SUMMARY
| Total of Sub Head 'A' | 2449063.471
| Total of Sub Head 'B' | 73420.36
| Total of Sub Head 'C' | 496836.1348
| Total of Non-Schedule Items | 254684.2
| TOTAL OF SCHEDULE "A, B, C" & NON SCHEDULE | 3274004.1658

## SUMMARY
R/M OF SESSI HOSPITALS , DESPENSERIES & DIRECTORATE OFFICE FOR F/Y 2015-16
SUMMARY OF ESTIMATED COST (CIVIL WORKS )
|  | (A) | (B) | ( C ) | (D) | ( E )
S.NO | NAME OF WORK | CIVIL WORKS MILLION | ROADS & PATHS MILLION | W/SUPPLY & S/W MILLION | NON -SCH. ITEMS MILLION | TOTAL NIT AMOUNT MILLION
1 | RENNOVATION ,REPAIR & MAINTENANCE OF SESSI LANDHI HOSPITAL KARACHI | 17.949 | 0.649 | 1.3831 | 0.9377 | 20.9188
2 | SPECIAL REPAIR & REHABILITATION OF OVER HEAD WATER TANK AT LANDHI HOSPITAL KARACHI | 0.45 | 0 | 0.45 | 1.85 | 2.75
3 | RENNOVATION, REPAIR & MAINTENANCE OF KBVS HOSPITAL SITE KARACHI MAIN HOSPITAL | 6.43 | 0.215 | 1.263 | 0.824 | 8.732
4 | RENNOVATION , REPAIR & MAINTENANCE OF KBVS HOSPITAL SITE KARACHI ( Emergency & Radiology Department ) | 4.896 | 0.042 | 0.496 | 0.234 | 5.668
5 | RENNOVATION , REPAIR & MAINTENANCE OF KBVS HOSPITAL SITE DOCTOR'SRESIDENCE | 5.005 | 0.157 | 0.77 | 1.158 | 7.09
R/M OF SESSI HOSPITALS , DESPENSERIES & DIRECTORATE OFFICE FOR F/Y 2015-16
SUMMARY OF ESTIMATED COST (CIVIL WORKS )
|  | (A) | (B) | ( C ) | (D) | ( E )
S.NO | NAME OF WORK | CIVIL WORKS MILLION | ROADS & PATHS MILLION | W/SUPPLY & S/W MILLION | NON -SCH. ITEMS MILLION | TOTAL NIT AMOUNT MILLION
6 | RENNOVATION, REPAIR & MAINTENANCE OF KBVS HOSPITAL SITE PARA MEDICAL RESIDENCE | 5.491 | 0.157 | 0.74 | 1.158 | 7.546
7 | RENNOVATION , REPAIR & MAINTENANCE OF CITY CIRCLE CLINIC LINES AREA G/ FLOOR CONSULTANT'S CLINIC REMAINING WORKS | 3.691 | 0.177 | 0.688 | 0.422 | 4.978
8 | RENNOVATION , REPAIR & MAINTENANCE OF CITY CIRCLE CLINIC LINES AREA EYE CLINIC FIRST FLOOR | 2.337 | 0.136 | 0.687 | 0.263 | 3.423
R/M OF SESSI HOSPITALS , DESPENSERIES & DIRECTORATE OFFICE FOR F/Y 2015-16
SUMMARY OF ESTIMATED COST (CIVIL WORKS )
|  | (A) | (B) | ( C ) | (D) | ( E )
S.NO | NAME OF WORK | CIVIL WORKS MILLION | ROADS & PATHS MILLION | W/SUPPLY & S/W MILLION | NON -SCH. ITEMS MILLION | TOTAL NIT AMOUNT MILLION
9 | RENNOVATION , REPAIR & MAINTENANCE OF PEER ABAD NEW GOLIMAR KARACHI | 2.337 | 0.136 | 0.688 | 0.263 | 3.424
10 | RENNOVATION , REPAIR & MAINTENANCE OF GANJU TAKAR CLINIC SITE HYDERABAD | 5.767 | 0.271 | 0.625 | 0.96 | 7.623
11 | SESSI HOSPITAL AT SITE AREA KOTRI (MAIN HOSPITAL ) | 5.295 | 1.016 | 0.691 | 0.452 | 7.454
12 | RENNOVATION , REPAIR & MAINTENANCE OF SESSI HOSPITAL AT SITE AREA KOTRI (DOCTOR'S RESIDENCE ) | 2.452 | 0.395 | 0.437 | 0.307 | 3.591
13 | RENNOVATION , REPAIR & MAINTENANCE OF SESSI HOSPITAL AT SITE AREA KOTRI (PARA MEDICAL STAFF RESIDENCE ) | 2.281 | 0.395 | 0.511 | 0.307 | 3.494
R/M OF SESSI HOSPITALS , DESPENSERIES & DIRECTORATE OFFICE FOR F/Y 2015-16
SUMMARY OF ESTIMATED COST (CIVIL WORKS )
|  | (A) | (B) | ( C ) | (D) | ( E )
S.NO | NAME OF WORK | CIVIL WORKS MILLION | ROADS & PATHS MILLION | W/SUPPLY & S/W MILLION | NON -SCH. ITEMS MILLION | TOTAL NIT AMOUNT MILLION
14 | RENOVATION, REPAIR , MAINTENANCE & ADDITION OF NEW BLOCK AT KOTRI DISPENSARY KOTRI SINDH | 15.25 | 1.524 | 0.654 | 0.465 | 17.893
15 | RENNOVATION , REPAIR & MAINTENANCE OF DISPENSARY AT SITE AREA SUKKUR | 4.727 | 0.102 | 0.631 | 0.44 | 5.9
16 | RENNOVATION, REPAIR & MAINTENANCE OF CIRCLE OFFICE AT SITE AREA SUKKUR | 4.536 | 0.102 | 0.656 | 0.423 | 5.717
17 | RENNOVATION , REPAIR & MAINTENNACE OF CITY DISPENSARY SUKKUR | 2.707 | 0.102 | 0.596 | 0.28 | 3.685
18 | RENNOVATION , REPAIR & MAINTENANCE OF MEDICAL CENTRE AT TANDO ADAM | 2.914 | 0.0734 | 0.496 | 0.254 | 3.7374
19 | RENNOVATION , REPAIR & MAINTENANCE OF DISPENSARY AT NOORIABAD | 2.449 | 0.0734 | 0.496 | 0.254 | 3.2724
| TOTAL FOR CIVIL WORKS |  |  |  | 11.2517 | 126.8966
R/M OF SESSI HOSPITALS , DESPENSERIES & DIRECTORATE OFFICE FOR F/Y 2015-16
SUMMARY OF ESTIMATED COST (ELECTRICAL WORKS )
|  | (A) | (B) | ( C ) | (D) | ( E )
S.NO | NAME OF WORK | ELECTRIC WORKS MILLION |  |  |  | TOTAL NIT AMOUNT MILLION
1 | RENNOVATION, REPAIR & MAINTENANCE SESSI LANDHI HOSPITAL KARACHI | 2.052 |  |  |  | 2.052
2 | SPECIAL REPAIR & REHABILITATION OF OVER HEAD WATER TANK AT LANDHI HOSPITAL KARACHI | 1.2 |  |  |  | 1.2
3 | RENNOVATION , REPAIR & MAINTENANCE OF KBVS HOSPITAL SITE KARACHI MAIN HOSPITAL | 1.443 |  |  |  | 1.443
4 | RENNOVATION , REPAIR & MAINTENANCE OF KBVS HOSPITAL SITE KARACHI ( Emergency & Radiology Department ) | 1.666 |  |  |  | 1.666
R/M OF SESSI HOSPITALS , DESPENSERIES & DIRECTORATE OFFICE FOR F/Y 2015-16
SUMMARY OF ESTIMATED COST (ELECTRICAL WORKS )
|  | (A) | (B) | ( C ) | (D) | ( E )
S.NO | NAME OF WORK | ELECTRIC WORKS MILLION |  |  |  | TOTAL NIT AMOUNT MILLION
5 | RENNOVATION , REPAIR & MAINTENANCE OF KBVS HOSPITAL SITE KARACHI DOCTOR'SRESIDENCE | 0.914 |  |  |  | 0.914
6 | RENNOVATION , REPAIR & MAINTENANCE OF KBVS HOSPITAL SITE ( PARA MEDICAL RESIDENCE ) | 0.915 |  |  |  | 0.915
7 | RENNOVATION , REPAIR & MAINTENANCE OF CITY CIRCLE CLINIC LINES AREA G/ FLOOR CONSULTANT"S CLINIC REMAINING WORKS | 0.805 |  |  |  | 0.805
R/M OF SESSI HOSPITALS , DESPENSERIES & DIRECTORATE OFFICE FOR F/Y 2015-16
SUMMARY OF ESTIMATED COST (ELECTRICAL WORKS )
|  | (A) | (B) | ( C ) | (D) | ( E )
S.NO | NAME OF WORK | ELECTRIC WORKS MILLION |  |  |  | TOTAL NIT AMOUNT MILLION
8 | RENNOVATION , REPAIR & MAINTENANCE OF CITY CIRCLE CLINIC LINES AREA EYE CLINIC FIRST FLOOR | 0.787 |  |  |  | 0.787
9 | RENNOVATION , REPAIR & MAINTENANCE OF PEER ABAD NEW GOLIMAR KARACHI | 0.805 |  |  |  | 0.805
10 | RENNOVATION ,REPAIR & MAINTENANCE OF GANJU TAKAR CLINIC SITE HYDERABAD | 1.12 |  |  |  | 1.12
11 | RENNOVATION , REPAIR & MAINTENANCE OF SESSI HOSPITAL AT SITE AREA KOTRI (MAIN HOSPITAL ) | 0.61 |  |  |  | 0.61
12 | RENNOVATION , REPAIR & MAINTENANCE OF SESSI HOSPITAL AT SITE AREA KOTRI (DOCTOR'S RESIDENCE ) | 0.506 |  |  |  | 0.506
R/M OF SESSI HOSPITALS , DESPENSERIES & DIRECTORATE OFFICE FOR F/Y 2015-16
SUMMARY OF ESTIMATED COST (ELECTRICAL WORKS )
|  | (A) | (B) | ( C ) | (D) | ( E )
S.NO | NAME OF WORK | ELECTRIC WORKS MILLION |  |  |  | TOTAL NIT AMOUNT MILLION
13 | RENNOVATION , REPAIR & MAINTENANCE OF SESSI HOSPITAL AT SITE AREA KOTRI (PARA MEDICAL STAFF RESIDENCE ) | 0.493 |  |  |  | 0.493
14 | RENOVATION, REPAIR , MAINTENANCE & ADDITION OF NEW BLOCK AT KOTRI DISPENSARY KOTRI SINDH | 2.15 |  |  |  | 2.15
15 | RENNOVATION , REPAIR & MAINTENANCE OF DISPENSARY AT SITE AREA SUKKUR | 1.27 |  |  |  | 1.27
16 | RENNOVATION , REPAIR & MAINTENANCE OF CIRCLE OFFICE AT SITE AREA SUKKUR | 0.999 |  |  |  | 0.999
17 | RENNOVATION , REPAIR & MAINTENANCE OF CITY DISPENSARY SUKKUR | 0.61 |  |  |  | 0.61
R/M OF SESSI HOSPITALS , DESPENSERIES & DIRECTORATE OFFICE FOR F/Y 2015-16
SUMMARY OF ESTIMATED COST (ELECTRICAL WORKS )
|  | (A) | (B) | ( C ) | (D) | ( E )
S.NO | NAME OF WORK | ELECTRIC WORKS MILLION |  |  |  | TOTAL NIT AMOUNT MILLION
18 | RENNOVATION , REPAIR & MAINTENACE OF MEDICAL CENTRE AT TANDO ADAM | 0.914 |  |  |  | 0.914
19 | RENNOVATION , REPAIR & MAINTENANCE OF DISPENSARY AT NOORIABAD | 0.96 |  |  |  | 0.96
| TOTAL FOR ELECTRICAL |  |  |  |  | 20.219
| TOTAL FOR CIVIL & ELECT. |  |  |  |  | 147.1156

## LANDHI (ELEC)
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI LANDHI HOSPITAL KARACHI
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 175 | Each | 109.34 | 19134.5
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 150 | Each | 28.04 | 4206
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 150 | Each | 279.46 | 41919
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 1 | Each | 1438.51 | 1438.51
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 1 | Each | 4131.38 | 4131.38
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 5 | Each | 1293.88 | 6469.4
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 40 | Each | 613.31 | 24532.4
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 20 | Each | 661.38 | 13227.6
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 8 | Each | 3823.88 | 30591.04
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 4 | Each | 4693.56 | 18774.24
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 3 | Each | 2033.56 | 6100.68
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 3563.51 | 7127.02
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 23.9 | 956
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 30 | Each | 28.64 | 859.2
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 36.55 | 731
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 20 | Each | 26.26 | 525.2
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 61.35 | 2454
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 108.32 | 4332.8
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 313.09 | 6261.8
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 117.88 | 2357.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 20 | Each | 53.94 | 1078.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 46.63 | 1865.2
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 25 | Each | 181.48 | 4537
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
0
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 534 | 5340
0
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
0
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 16 | Each | 237 | 3792
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 10 | Each | 784 | 7840
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 150 | Point | 767.28 | 115092
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 848 | 16960
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 20 | Point | 1064.88 | 21297.6
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 380.78 | 19039
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 250 | Point | 675.32 | 168830
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 40 | Point | 913.49 | 36539.6
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 777.84 | 15556.8
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 40 | Point | 350.64 | 14025.6
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 25 | Point | 339.31 | 8482.75
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 215 | Rft | 36.55 | 7858.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 28.85 | 4327.5
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 110 | Rft | 32.59 | 3584.9
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 325 | Rft | 44.48 | 14456
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.67 | 5500.5
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 155 | Rft | 35.02 | 5428.1
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 32.85 | 4927.5
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 250 | Rft | 35.42 | 8855
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 450 | Rft | 44.08 | 19836
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 250 | Rft | 38.02 | 9505
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 125 | Rft | 38.81 | 4851.25
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 150 | Rft | 56.69 | 8503.5
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 350 | Rft | 60.27 | 21094.5
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 72.27 | 18067.5
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 150 | Rft | 93.33 | 13999.5
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 131.03 | 32757.5
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 150 | Rft | 78.72 | 11808
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 250 | Rft | 105.71 | 26427.5
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 350 | Rft | 136.58 | 47803
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 350 | Each | 27.38 | 9583
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 50 | Each | 26.62 | 1331
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 45 | Each | 65.96 | 2968.2
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 25 | Each | 119.81 | 2995.25
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 20 | Each | 195.6 | 3912
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 20 | Each | 128.24 | 2564.8
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 250 | Each | 47.13 | 11782.5
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 20 | Each | 138.22 | 2764.4
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 15 | Each | 290.84 | 4362.6
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 25 | Each | 514.58 | 12864.5
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 20 | Each | 565.84 | 11316.8
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 45 | Each | 1803.45 | 81155.25
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 15 | Each | 4155.25 | 62328.75
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4911.5 | 19646
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 5 | Each | 2238.5 | 11192.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 25 | P/Sft | 2420 | 60500
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 5 | Each | 1765.5 | 8827.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 5 | Set | 220 | 1100
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 2 | Each | 2524.5 | 5049
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 1 | Each | 7557 | 7557
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 45 | Each | 2018 | 90810
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 40 | Each | 1897 | 75880
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 20 | Each | 572 | 11440
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 100 | Each | 376 | 37600
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 20 | Each | 359 | 7180
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 40 | Each | 277 | 11080
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 15 | Each | 589 | 8835
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 40 | Each | 2031 | 81240
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 10 | Each | 7158 | 71580
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 30 | Each | 2088 | 62640
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1884 | 18840
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1866 | 9330
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1400 | 8400
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1286 | 12860
| LT CABLES |  |  |  | 0
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 150 | Rft | 217.8 | 32670
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 60 | Rft | 332.75 | 19965
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 2 | Job | 8358 | 16716
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 2650 | Cft | 3.63 | 9619.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 2 | Each | 8566 | 17132
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 2 | Each | 6533 | 13066
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 1 | Each | 8476 | 8476
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 2 | Each | 7947 | 15894
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 3 | Each | 3245 | 9735
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 120 | 100 Cft | 10063 | 12075.6
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 20 | Each | 65 | 1300
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 80 | Rft | 93.32 | 7465.6
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 16 | Each | 389 | 6224
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 4 | Each | 571 | 2284
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 2051508.3

## KBVS HOS ELECT
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL SITE KARACHI
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 275 | Each | 109.34 | 30068.5
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 150 | Each | 28.04 | 4206
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 200 | Each | 279.46 | 55892
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 1 | Each | 1438.51 | 1438.51
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 1 | Each | 4131.38 | 4131.38
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 5 | Each | 1293.88 | 6469.4
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 40 | Each | 613.31 | 24532.4
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 20 | Each | 661.38 | 13227.6
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 8 | Each | 3823.88 | 30591.04
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 4 | Each | 4693.56 | 18774.24
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 3 | Each | 2033.56 | 6100.68
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 3563.51 | 7127.02
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 28.59 | 1143.6
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 23.9 | 956
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.64 | 572.8
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 36.55 | 1462
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 20 | Each | 26.26 | 525.2
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 61.35 | 2454
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 60 | Each | 108.32 | 6499.2
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 313.09 | 6261.8
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 117.88 | 2357.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 20 | Each | 53.94 | 1078.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 46.63 | 1865.2
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 25 | Each | 181.48 | 4537
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
0
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 534 | 5340
0
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
0
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 16 | Each | 237 | 3792
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 15 | Each | 784 | 11760
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 767.28 | 38364
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 40 | Point | 848 | 33920
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 30 | Point | 1064.88 | 31946.4
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 380.78 | 19039
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 10 | Point | 675.32 | 6753.2
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 913.49 | 9134.9
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 777.84 | 15556.8
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 350.64 | 3506.4
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 10 | Point | 339.31 | 3393.1
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 215 | Rft | 36.55 | 7858.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 25 | Rft | 28.85 | 721.25
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 125 | Rft | 44.48 | 5560
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.67 | 5500.5
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 120 | Rft | 35.02 | 4202.4
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 32.85 | 3942
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 35.42 | 4250.4
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 225 | Rft | 44.08 | 9918
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 20 | Rft | 38.02 | 760.4
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 38.81 | 1164.3
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 56.69 | 1700.7
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 40 | Rft | 60.27 | 2410.8
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 72.27 | 1806.75
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 20 | Rft | 93.33 | 1866.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 131.03 | 3275.75
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 50 | Rft | 78.72 | 3936
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 30 | Rft | 105.71 | 3171.3
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 350 | Rft | 136.58 | 47803
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 250 | Each | 27.38 | 6845
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 50 | Each | 26.62 | 1331
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 45 | Each | 65.96 | 2968.2
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 25 | Each | 119.81 | 2995.25
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 20 | Each | 195.6 | 3912
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 20 | Each | 128.24 | 2564.8
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 150 | Each | 47.13 | 7069.5
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 15 | Each | 290.84 | 4362.6
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 25 | Each | 514.58 | 12864.5
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 20 | Each | 565.84 | 11316.8
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 30 | Each | 1803.45 | 54103.5
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 10 | Each | 4155.25 | 41552.5
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4911.5 | 19646
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 5 | Each | 2238.5 | 11192.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 35 | P/Sft | 2420 | 84700
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 30 | P/Sft | 4372.5 | 131175
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 5 | Each | 1765.5 | 8827.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 5 | Set | 220 | 1100
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 2 | Each | 2524.5 | 5049
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 1 | Each | 7557 | 7557
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 10 | Each | 2018 | 20180
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 10 | Each | 1897 | 18970
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 10 | Each | 572 | 5720
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 25 | Each | 376 | 9400
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 20 | Each | 359 | 7180
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 40 | Each | 277 | 11080
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 15 | Each | 589 | 8835
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 30 | Each | 2031 | 60930
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 10 | Each | 7158 | 71580
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 20 | Each | 2088 | 41760
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1884 | 18840
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1866 | 9330
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 12 | Each | 1400 | 16800
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 20 | Each | 1286 | 25720
LT CABLES
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 75 | Rft | 217.8 | 16335
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 35 | Rft | 332.75 | 11646.25
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 1650 | Cft | 3.63 | 5989.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 2 | Each | 8566 | 17132
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 1 | Each | 8476 | 8476
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 1 | Each | 7947 | 7947
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 3 | Each | 3245 | 9735
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 75 | 100 Cft | 10063 | 7547.25
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 12 | Each | 65 | 780
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 60 | Rft | 93.32 | 5599.2
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 16 | Each | 389 | 6224
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 4 | Each | 571 | 2284
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 1443358.65

## KBVS Emer. Elect
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KVSS HOSPITAL SITE KARACHI (Emergency ward & Radiology Department)
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 20 | Each | 109.34 | 2186.8
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 20 | Each | 28.04 | 560.8
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 30 | Each | 279.46 | 8383.8
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 4 | Each | 613.31 | 2453.24
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 661.38 | 1322.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 4 | Each | 3823.88 | 15295.52
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 4693.56 | 9387.12
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 2033.56 | 2033.56
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 3563.51 | 7127.02
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 23.9 | 956
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 28.64 | 286.4
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 36.55 | 731
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 20 | Each | 26.26 | 525.2
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 61.35 | 1227
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 108.32 | 1083.2
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 313.09 | 3130.9
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 117.88 | 1178.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 10 | Each | 53.94 | 539.4
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 46.63 | 233.15
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 181.48 | 907.4
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 0 | Each | 534 | 0
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 0 | Each | 237 | 0
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 0 | Each | 784 | 0
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 40 | Point | 767.28 | 30691.2
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 848 | 8480
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 1064.88 | 10648.8
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 380.78 | 3807.8
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 40 | Point | 675.32 | 27012.8
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 30 | Point | 913.49 | 27404.7
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 777.84 | 7778.4
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 350.64 | 7012.8
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 20 | Point | 339.31 | 6786.2
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.55 | 5482.5
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 28.85 | 4327.5
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 110 | Rft | 32.59 | 3584.9
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 325 | Rft | 44.48 | 14456
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.67 | 5500.5
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 155 | Rft | 35.02 | 5428.1
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 32.85 | 4927.5
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 50 | Rft | 35.42 | 1771
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 450 | Rft | 44.08 | 19836
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 250 | Rft | 38.02 | 9505
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 125 | Rft | 38.81 | 4851.25
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 150 | Rft | 56.69 | 8503.5
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 60.27 | 15067.5
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 72.27 | 18067.5
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 150 | Rft | 93.33 | 13999.5
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 131.03 | 32757.5
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 0 | Rft | 78.72 | 0
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 0 | Rft | 105.71 | 0
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 0 | Rft | 78.81 | 0
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 0 | Rft | 136.58 | 0
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 50 | Each | 27.38 | 1369
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 10 | Each | 26.62 | 266.2
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 10 | Each | 65.96 | 659.6
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 10 | Each | 119.81 | 1198.1
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 10 | Each | 195.6 | 1956
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 15 | Each | 128.24 | 1923.6
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 60 | Each | 47.13 | 2827.8
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 20 | Each | 138.22 | 2764.4
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 15 | Each | 290.84 | 4362.6
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 25 | Each | 514.58 | 12864.5
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 20 | Each | 565.84 | 11316.8
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 20 | Each | 1803.45 | 36069
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 10 | Each | 4155.25 | 41552.5
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 2 | Each | 4911.5 | 9823
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 4 | Each | 2238.5 | 8954
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 25 | P/Sft | 2420 | 60500
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 2 | Each | 1765.5 | 3531
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 5 | Set | 220 | 1100
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 0 | Each | 2524.5 | 0
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 0 | Each | 7557 | 0
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 25 | Each | 2018 | 50450
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 20 | Each | 1897 | 37940
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 20 | Each | 572 | 11440
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 40 | Each | 376 | 15040
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 20 | Each | 359 | 7180
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 10 | Each | 277 | 2770
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 10 | Each | 589 | 5890
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 0 | Each | 2031 | 0
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 20 | Each | 2088 | 41760
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1884 | 9420
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1866 | 9330
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 4 | Each | 1400 | 5600
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1286 | 6430
LT CABLES
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 45 | Rft | 217.8 | 9801
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 2650 | Cft | 3.63 | 9619.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 0 | Each | 8476 | 0
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 0 | Each | 7947 | 0
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 0 | Each | 3245 | 0
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 0 | 100 Cft | 10063 | 0
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 0 | Each | 65 | 0
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 0 | Rft | 93.32 | 0
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 0 | Each | 389 | 0
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 0 | Each | 571 | 0
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 943835.45

## KBVS DOCTOR'S RES ELECT
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL ( DOCTOR'S RESIDENCE ) SITE KARACHI
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 20 | Each | 109.34 | 2186.8
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 30 | Each | 28.04 | 841.2
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 55 | Each | 279.46 | 15370.3
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 15 | Each | 613.31 | 9199.65
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 661.38 | 3306.9
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 3823.88 | 7647.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 4693.56 | 9387.12
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 2033.56 | 4067.12
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 3563.51 | 7127.02
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 28.59 | 1143.6
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 30 | Each | 23.9 | 717
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.64 | 572.8
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 5 | Each | 26.26 | 131.3
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 15 | Each | 61.35 | 920.25
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 15 | Each | 108.32 | 1624.8
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 313.09 | 3130.9
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 117.88 | 2357.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 20 | Each | 53.94 | 1078.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 46.63 | 233.15
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 181.48 | 907.4
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
0
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 534 | 5340
0
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
0
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 0 | Each | 237 | 0
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 0 | Each | 784 | 0
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 25 | Point | 767.28 | 19182
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 848 | 16960
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 18 | Point | 1064.88 | 19167.84
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 40 | Point | 380.78 | 15231.2
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 10 | Point | 675.32 | 6753.2
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 40 | Point | 913.49 | 36539.6
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 777.84 | 15556.8
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 350.64 | 3506.4
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 10 | Point | 339.31 | 3393.1
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 215 | Rft | 36.55 | 7858.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 25 | Rft | 28.85 | 721.25
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 125 | Rft | 44.48 | 5560
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.67 | 5500.5
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 120 | Rft | 35.02 | 4202.4
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 32.85 | 3942
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 35.42 | 4250.4
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 225 | Rft | 44.08 | 9918
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 20 | Rft | 38.02 | 760.4
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 38.81 | 1164.3
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 56.69 | 1700.7
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 40 | Rft | 60.27 | 2410.8
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 72.27 | 1806.75
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 20 | Rft | 93.33 | 1866.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 131.03 | 3275.75
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 20 | Rft | 78.72 | 1574.4
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 30 | Rft | 105.71 | 3171.3
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 150 | Rft | 136.58 | 20487
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 60 | Each | 27.38 | 1642.8
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 30 | Each | 26.62 | 798.6
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 15 | Each | 65.96 | 989.4
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 25 | Each | 119.81 | 2995.25
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 18 | Each | 195.6 | 3520.8
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 20 | Each | 128.24 | 2564.8
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 150 | Each | 47.13 | 7069.5
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 15 | Each | 290.84 | 4362.6
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 25 | Each | 514.58 | 12864.5
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 20 | Each | 565.84 | 11316.8
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 5 | Each | 1803.45 | 9017.25
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4155.25 | 16621
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 2 | Each | 4911.5 | 9823
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 6 | Each | 2238.5 | 13431
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 35 | P/Sft | 2420 | 84700
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 30 | P/Sft | 4372.5 | 131175
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 6 | Each | 1765.5 | 10593
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 6 | Set | 220 | 1320
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 2 | Each | 2524.5 | 5049
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 1 | Each | 7557 | 7557
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 10 | Each | 2018 | 20180
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 10 | Each | 1897 | 18970
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 10 | Each | 572 | 5720
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 25 | Each | 376 | 9400
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 20 | Each | 359 | 7180
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 20 | Each | 277 | 5540
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 10 | Each | 589 | 5890
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 0 | Each | 2031 | 0
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 2088 | 20880
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1884 | 11304
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1866 | 18660
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1400 | 8400
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1286 | 12860
LT CABLES
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 75 | Rft | 217.8 | 16335
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 0 | Job | 8358 | 0
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 650 | Cft | 3.63 | 2359.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 1 | Each | 8476 | 8476
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 1 | Each | 7947 | 7947
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 3 | Each | 3245 | 9735
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 60 | 100 Cft | 10063 | 6037.8
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 9 | Each | 65 | 585
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 60 | Rft | 93.32 | 5599.2
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 16 | Each | 389 | 6224
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 4 | Each | 571 | 2284
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 913883.34

## KBVS PARA MED RES ELECT.
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KBVS HOSPITAL ( PARA MEDICAL STAFF'S RESIDENCE ) SITE KARACHI
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 20 | Each | 109.34 | 2186.8
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 30 | Each | 28.04 | 841.2
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 65 | Each | 279.46 | 18164.9
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 10 | Each | 613.31 | 6133.1
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 661.38 | 3306.9
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 3823.88 | 7647.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 4693.56 | 9387.12
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 2033.56 | 4067.12
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 3563.51 | 7127.02
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 28.59 | 1143.6
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 30 | Each | 23.9 | 717
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 28.64 | 286.4
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 5 | Each | 26.26 | 131.3
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 15 | Each | 61.35 | 920.25
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 15 | Each | 108.32 | 1624.8
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 313.09 | 3130.9
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 117.88 | 2357.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 20 | Each | 53.94 | 1078.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 46.63 | 233.15
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 181.48 | 907.4
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
0
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 534 | 5340
0
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
0
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 0 | Each | 237 | 0
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 0 | Each | 784 | 0
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 35 | Point | 767.28 | 26854.8
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 30 | Point | 848 | 25440
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 18 | Point | 1064.88 | 19167.84
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 40 | Point | 380.78 | 15231.2
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 30 | Point | 675.32 | 20259.6
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 20 | Point | 913.49 | 18269.8
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 0 | Point | 777.84 | 0
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 350.64 | 7012.8
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 10 | Point | 339.31 | 3393.1
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 215 | Rft | 36.55 | 7858.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 25 | Rft | 28.85 | 721.25
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 125 | Rft | 44.48 | 5560
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.67 | 5500.5
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 120 | Rft | 35.02 | 4202.4
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 32.85 | 3942
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 35.42 | 4250.4
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 225 | Rft | 44.08 | 9918
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 20 | Rft | 38.02 | 760.4
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 38.81 | 1164.3
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 56.69 | 1700.7
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 40 | Rft | 60.27 | 2410.8
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 72.27 | 1806.75
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 20 | Rft | 93.33 | 1866.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 131.03 | 3275.75
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 20 | Rft | 78.72 | 1574.4
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 30 | Rft | 105.71 | 3171.3
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 150 | Rft | 136.58 | 20487
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 60 | Each | 27.38 | 1642.8
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 30 | Each | 26.62 | 798.6
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 15 | Each | 65.96 | 989.4
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 25 | Each | 119.81 | 2995.25
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 18 | Each | 195.6 | 3520.8
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 20 | Each | 128.24 | 2564.8
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 200 | Each | 47.13 | 9426
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 15 | Each | 290.84 | 4362.6
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 25 | Each | 514.58 | 12864.5
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 20 | Each | 565.84 | 11316.8
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 5 | Each | 1803.45 | 9017.25
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4155.25 | 16621
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 2 | Each | 4911.5 | 9823
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 6 | Each | 2238.5 | 13431
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 35 | P/Sft | 2420 | 84700
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 30 | P/Sft | 4372.5 | 131175
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 6 | Each | 1765.5 | 10593
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 6 | Set | 220 | 1320
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 2 | Each | 2524.5 | 5049
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 1 | Each | 7557 | 7557
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 10 | Each | 2018 | 20180
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 10 | Each | 1897 | 18970
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 10 | Each | 572 | 5720
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 25 | Each | 376 | 9400
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 20 | Each | 359 | 7180
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 20 | Each | 277 | 5540
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 10 | Each | 589 | 5890
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 0 | Each | 2031 | 0
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 2088 | 20880
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1884 | 11304
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1866 | 18660
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1400 | 8400
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1286 | 12860
LT CABLES
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 75 | Rft | 217.8 | 16335
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 0 | Job | 8358 | 0
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 650 | Cft | 3.63 | 2359.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 1 | Each | 8476 | 8476
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 1 | Each | 7947 | 7947
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 3 | Each | 3245 | 9735
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 60 | 100 Cft | 10063 | 6037.8
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 9 | Each | 65 | 585
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 60 | Rft | 93.32 | 5599.2
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 16 | Each | 389 | 6224
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 4 | Each | 571 | 2284
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 915020.49

## HYDERABAD ELECT.
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF HYDERABAD DISPENCERIES AT GANJU TAKAR SITE HYDERABAD
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 20 | Each | 109.34 | 2186.8
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 20 | Each | 28.04 | 560.8
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 30 | Each | 279.46 | 8383.8
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 1 | Each | 1438.51 | 1438.51
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 1 | Each | 4131.38 | 4131.38
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 10 | Each | 613.31 | 6133.1
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 10 | Each | 661.38 | 6613.8
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 4 | Each | 3823.88 | 15295.52
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 4693.56 | 9387.12
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 2033.56 | 2033.56
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 3563.51 | 3563.51
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 23.9 | 239
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.64 | 572.8
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 36.55 | 731
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 5 | Each | 26.26 | 131.3
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 61.35 | 613.5
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 108.32 | 1083.2
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 313.09 | 3130.9
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 117.88 | 2357.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 10 | Each | 53.94 | 539.4
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 46.63 | 932.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 15 | Each | 181.48 | 2722.2
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 534 | 5340
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 8 | Each | 237 | 1896
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 5 | Each | 784 | 3920
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 767.28 | 38364
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 40 | Point | 848 | 33920
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 30 | Point | 1064.88 | 31946.4
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 380.78 | 19039
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 10 | Point | 675.32 | 6753.2
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 913.49 | 9134.9
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 777.84 | 15556.8
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 350.64 | 3506.4
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 10 | Point | 339.31 | 3393.1
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 115 | Rft | 36.55 | 4203.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 25 | Rft | 28.85 | 721.25
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 125 | Rft | 44.48 | 5560
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.67 | 5500.5
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 120 | Rft | 35.02 | 4202.4
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 32.85 | 3942
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 35.42 | 4250.4
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 125 | Rft | 44.08 | 5510
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 20 | Rft | 38.02 | 760.4
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 38.81 | 1164.3
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 56.69 | 1700.7
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 40 | Rft | 60.27 | 2410.8
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 72.27 | 1806.75
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 20 | Rft | 93.33 | 1866.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 131.03 | 3275.75
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 25 | Rft | 78.72 | 1968
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 30 | Rft | 105.71 | 3171.3
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 50 | Rft | 136.58 | 6829
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 25 | Each | 27.38 | 684.5
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 20 | Each | 26.62 | 532.4
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 10 | Each | 65.96 | 659.6
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 15 | Each | 119.81 | 1797.15
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 10 | Each | 195.6 | 1956
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 10 | Each | 128.24 | 1282.4
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 45 | Each | 47.13 | 2120.85
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 15 | Each | 290.84 | 4362.6
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 15 | Each | 514.58 | 7718.7
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 15 | Each | 565.84 | 8487.6
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 30 | Each | 50.65 | 1519.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 20 | Each | 1803.45 | 36069
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 10 | Each | 4155.25 | 41552.5
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4911.5 | 19646
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 5 | Each | 2238.5 | 11192.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 35 | P/Sft | 2420 | 84700
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 30 | P/Sft | 4372.5 | 131175
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 5 | Each | 1765.5 | 8827.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 5 | Set | 220 | 1100
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 2 | Each | 2524.5 | 5049
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 1 | Each | 7557 | 7557
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 20 | Each | 2018 | 40360
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 10 | Each | 1897 | 18970
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 10 | Each | 572 | 5720
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 25 | Each | 376 | 9400
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 20 | Each | 359 | 7180
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 30 | Each | 277 | 8310
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 15 | Each | 589 | 8835
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 30 | Each | 2031 | 60930
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 10 | Each | 7158 | 71580
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 20 | Each | 2088 | 41760
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1884 | 18840
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1866 | 9330
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1400 | 8400
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1286 | 12860
LT CABLES
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 75 | Rft | 217.8 | 16335
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 650 | Cft | 3.63 | 2359.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 0 | Each | 8566 | 0
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 0 | Each | 8476 | 0
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 1 | Each | 7947 | 7947
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 2 | Each | 3245 | 6490
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 50 | 100 Cft | 10063 | 5031.5
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 12 | Each | 65 | 780
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 30 | Rft | 93.32 | 2799.6
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 6 | Each | 389 | 2334
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 2 | Each | 571 | 1142
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 1119696.93

## LINES AREA EYE CLINIC ELECT.
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (FIRST FLOOR ENT CLINIC FIRST FLOOR )
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 10 | Each | 109.34 | 1093.4
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 10 | Each | 28.04 | 280.4
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 20 | Each | 279.46 | 5589.2
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 1 | Each | 1438.51 | 1438.51
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 1 | Each | 4131.38 | 4131.38
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 613.31 | 3066.55
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 661.38 | 3306.9
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 3823.88 | 7647.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 4693.56 | 9387.12
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 2033.56 | 2033.56
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 3563.51 | 3563.51
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 23.9 | 239
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 28.64 | 286.4
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 5 | Each | 26.26 | 131.3
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 61.35 | 613.5
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 108.32 | 1083.2
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 313.09 | 3130.9
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 117.88 | 2357.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 10 | Each | 53.94 | 539.4
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 46.63 | 932.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 181.48 | 907.4
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 534 | 2670
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 89 | 445
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 5 | Each | 237 | 1185
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 5 | Each | 784 | 3920
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 767.28 | 38364
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 30 | Point | 848 | 25440
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 20 | Point | 1064.88 | 21297.6
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 380.78 | 19039
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 10 | Point | 675.32 | 6753.2
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 913.49 | 9134.9
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 777.84 | 15556.8
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 350.64 | 3506.4
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 10 | Point | 339.31 | 3393.1
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 115 | Rft | 36.55 | 4203.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 25 | Rft | 28.85 | 721.25
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 125 | Rft | 44.48 | 5560
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.67 | 5500.5
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 80 | Rft | 35.02 | 2801.6
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 60 | Rft | 32.85 | 1971
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 60 | Rft | 35.42 | 2125.2
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 25 | Rft | 44.08 | 1102
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 20 | Rft | 38.02 | 760.4
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 38.81 | 1164.3
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 56.69 | 1700.7
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 40 | Rft | 60.27 | 2410.8
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 72.27 | 1806.75
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 20 | Rft | 93.33 | 1866.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 131.03 | 3275.75
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 25 | Rft | 78.72 | 1968
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 30 | Rft | 105.71 | 3171.3
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 30 | Rft | 136.58 | 4097.4
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 25 | Each | 27.38 | 684.5
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 20 | Each | 26.62 | 532.4
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 10 | Each | 65.96 | 659.6
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 15 | Each | 119.81 | 1797.15
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 10 | Each | 195.6 | 1956
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 10 | Each | 128.24 | 1282.4
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 30 | Each | 47.13 | 1413.9
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 10 | Each | 290.84 | 2908.4
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 15 | Each | 514.58 | 7718.7
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 15 | Each | 565.84 | 8487.6
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 30 | Each | 50.65 | 1519.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 20 | Each | 1803.45 | 36069
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 10 | Each | 4155.25 | 41552.5
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4911.5 | 19646
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 5 | Each | 2238.5 | 11192.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 15 | P/Sft | 2420 | 36300
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 15 | P/Sft | 4372.5 | 65587.5
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 5 | Each | 1765.5 | 8827.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 5 | Set | 220 | 1100
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 2 | Each | 2524.5 | 5049
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 1 | Each | 7557 | 7557
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 15 | Each | 2018 | 30270
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 10 | Each | 1897 | 18970
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 10 | Each | 572 | 5720
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 20 | Each | 376 | 7520
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 15 | Each | 359 | 5385
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 20 | Each | 277 | 5540
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 10 | Each | 589 | 5890
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 20 | Each | 2031 | 40620
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 2088 | 20880
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1884 | 9420
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 4 | Each | 1866 | 7464
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 4 | Each | 1400 | 5600
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1286 | 6430
LT CABLES
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 75 | Rft | 217.8 | 16335
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 650 | Cft | 3.63 | 2359.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 0 | Each | 8566 | 0
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 0 | Each | 8476 | 0
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 0 | Each | 7947 | 0
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 2 | Each | 3245 | 6490
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 50 | 100 Cft | 10063 | 5031.5
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 12 | Each | 65 | 780
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 30 | Rft | 93.32 | 2799.6
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 6 | Each | 389 | 2334
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 2 | Each | 571 | 1142
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 786587.57

## LINES AREA CONS'S CLINIC ELEC.
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY CIRCLE CLINIC LINES AREA KARACHI (CONSULTANT'S CLINIC AT GROUND FLOOR )
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 0 | Each | 109.34 | 0
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 0 | Each | 28.04 | 0
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 5 | Each | 279.46 | 1397.3
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 4 | Each | 613.31 | 2453.24
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 4 | Each | 661.38 | 2645.52
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 3823.88 | 7647.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 4693.56 | 9387.12
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 2033.56 | 2033.56
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 3563.51 | 3563.51
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 23.9 | 119.5
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 28.64 | 143.2
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 36.55 | 182.75
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 5 | Each | 26.26 | 131.3
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 61.35 | 306.75
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 108.32 | 541.6
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 313.09 | 1565.45
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 117.88 | 1178.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 5 | Each | 53.94 | 269.7
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 46.63 | 93.26
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 181.48 | 362.96
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 534 | 2670
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 89 | 445
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 0 | Each | 237 | 0
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 0 | Each | 784 | 0
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 767.28 | 38364
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 30 | Point | 848 | 25440
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 20 | Point | 1064.88 | 21297.6
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 30 | Point | 380.78 | 11423.4
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 0 | Point | 675.32 | 0
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 0 | Point | 913.49 | 0
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 0 | Point | 777.84 | 0
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 0 | Point | 350.64 | 0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 10 | Point | 339.31 | 3393.1
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 45 | Rft | 36.55 | 1644.75
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 25 | Rft | 28.85 | 721.25
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 40 | Rft | 32.59 | 1303.6
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 40 | Rft | 44.48 | 1779.2
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 60 | Rft | 36.67 | 2200.2
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 80 | Rft | 35.02 | 2801.6
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 0 | Rft | 32.85 | 0
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 0 | Rft | 35.42 | 0
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 0 | Rft | 44.08 | 0
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 0 | Rft | 38.02 | 0
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 38.81 | 1164.3
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 56.69 | 1700.7
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 40 | Rft | 60.27 | 2410.8
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 72.27 | 1806.75
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 20 | Rft | 93.33 | 1866.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 131.03 | 3275.75
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 25 | Rft | 78.72 | 1968
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 30 | Rft | 105.71 | 3171.3
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 30 | Rft | 136.58 | 4097.4
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 25 | Each | 27.38 | 684.5
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 20 | Each | 26.62 | 532.4
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 10 | Each | 65.96 | 659.6
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 15 | Each | 119.81 | 1797.15
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 10 | Each | 195.6 | 1956
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 10 | Each | 128.24 | 1282.4
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 30 | Each | 47.13 | 1413.9
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 10 | Each | 290.84 | 2908.4
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 15 | Each | 514.58 | 7718.7
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 15 | Each | 565.84 | 8487.6
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 30 | Each | 50.65 | 1519.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 20 | Each | 1803.45 | 36069
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 10 | Each | 4155.25 | 41552.5
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4911.5 | 19646
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 5 | Each | 2238.5 | 11192.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 15 | P/Sft | 2420 | 36300
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 15 | P/Sft | 4372.5 | 65587.5
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 5 | Each | 1765.5 | 8827.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 5 | Set | 220 | 1100
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 2 | Each | 2524.5 | 5049
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 1 | Each | 7557 | 7557
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 15 | Each | 2018 | 30270
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 10 | Each | 1897 | 18970
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 10 | Each | 572 | 5720
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 10 | Each | 376 | 3760
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 15 | Each | 359 | 5385
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 25 | Each | 277 | 6925
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 20 | Each | 589 | 11780
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 50 | Each | 2031 | 101550
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 2088 | 10440
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 25 | Each | 1884 | 47100
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1866 | 18660
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 4 | Each | 1400 | 5600
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1286 | 6430
LT CABLES
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 75 | Rft | 217.8 | 16335
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 650 | Cft | 3.63 | 2359.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 0 | Each | 8566 | 0
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 0 | Each | 8476 | 0
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 0 | Each | 7947 | 0
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 2 | Each | 3245 | 6490
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 50 | 100 Cft | 10063 | 5031.5
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 8 | Each | 65 | 520
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 20 | Rft | 93.32 | 1866.4
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 4 | Each | 389 | 1556
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 1 | Each | 571 | 571
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 804902.66

## PEER ABAD DESP
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF PEERABAD NEW GOLIMAR KARACHI
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 10 | Each | 109.34 | 1093.4
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 10 | Each | 28.04 | 280.4
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 20 | Each | 279.46 | 5589.2
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 1 | Each | 1438.51 | 1438.51
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 1 | Each | 4131.38 | 4131.38
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 613.31 | 3066.55
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 661.38 | 3306.9
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 3823.88 | 7647.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 4693.56 | 9387.12
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 2033.56 | 2033.56
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 3563.51 | 3563.51
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 23.9 | 239
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 28.64 | 286.4
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 5 | Each | 26.26 | 131.3
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 61.35 | 613.5
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 108.32 | 1083.2
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 313.09 | 3130.9
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 117.88 | 2357.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 10 | Each | 53.94 | 539.4
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 46.63 | 932.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 181.48 | 907.4
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 534 | 2670
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 89 | 445
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 5 | Each | 237 | 1185
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 5 | Each | 784 | 3920
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 767.28 | 38364
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 30 | Point | 848 | 25440
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 20 | Point | 1064.88 | 21297.6
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 380.78 | 19039
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 10 | Point | 675.32 | 6753.2
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 913.49 | 9134.9
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 777.84 | 15556.8
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 350.64 | 3506.4
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 10 | Point | 339.31 | 3393.1
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 115 | Rft | 36.55 | 4203.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 25 | Rft | 28.85 | 721.25
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 125 | Rft | 44.48 | 5560
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.67 | 5500.5
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 80 | Rft | 35.02 | 2801.6
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 60 | Rft | 32.85 | 1971
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 60 | Rft | 35.42 | 2125.2
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 25 | Rft | 44.08 | 1102
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 20 | Rft | 38.02 | 760.4
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 38.81 | 1164.3
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 56.69 | 1700.7
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 40 | Rft | 60.27 | 2410.8
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 72.27 | 1806.75
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 20 | Rft | 93.33 | 1866.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 25 | Rft | 131.03 | 3275.75
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 25 | Rft | 78.72 | 1968
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 30 | Rft | 105.71 | 3171.3
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 30 | Rft | 136.58 | 4097.4
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 25 | Each | 27.38 | 684.5
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 20 | Each | 26.62 | 532.4
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 10 | Each | 65.96 | 659.6
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 15 | Each | 119.81 | 1797.15
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 10 | Each | 195.6 | 1956
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 10 | Each | 128.24 | 1282.4
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 30 | Each | 47.13 | 1413.9
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 10 | Each | 290.84 | 2908.4
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 15 | Each | 514.58 | 7718.7
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 15 | Each | 565.84 | 8487.6
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 30 | Each | 50.65 | 1519.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 20 | Each | 1803.45 | 36069
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 10 | Each | 4155.25 | 41552.5
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4911.5 | 19646
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 5 | Each | 2238.5 | 11192.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 15 | P/Sft | 2420 | 36300
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 15 | P/Sft | 4372.5 | 65587.5
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 5 | Each | 1765.5 | 8827.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 5 | Set | 220 | 1100
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 2 | Each | 2524.5 | 5049
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 1 | Each | 7557 | 7557
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 15 | Each | 2018 | 30270
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 10 | Each | 1897 | 18970
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 10 | Each | 572 | 5720
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 20 | Each | 376 | 7520
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 15 | Each | 359 | 5385
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 20 | Each | 277 | 5540
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 10 | Each | 589 | 5890
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 20 | Each | 2031 | 40620
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 2088 | 20880
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1884 | 9420
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 4 | Each | 1866 | 7464
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 4 | Each | 1400 | 5600
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1286 | 6430
LT CABLES
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 75 | Rft | 217.8 | 16335
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 650 | Cft | 3.63 | 2359.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved. | 0 | Each | 8566 | 0
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved. | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved. | 0 | Each | 8476 | 0
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved. | 0 | Each | 7947 | 0
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 2 | Each | 3245 | 6490
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 50 | 100 Cft | 10063 | 5031.5
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 12 | Each | 65 | 780
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 30 | Rft | 93.32 | 2799.6
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make. | 6 | Each | 389 | 2334
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make. | 2 | Each | 571 | 1142
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 786587.57

## SUKKUR DISPENSERY ELECT.
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF DISPENSARY AT SITE AREA SUKKUR
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 20 | Each | 109.34 | 2186.8
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 25 | Each | 28.04 | 701
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 45 | Each | 279.46 | 12575.7
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 20 | Each | 613.31 | 12266.2
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 10 | Each | 661.38 | 6613.8
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 4 | Each | 3823.88 | 15295.52
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 4693.56 | 9387.12
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 2033.56 | 4067.12
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 3563.51 | 7127.02
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 23.9 | 478
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 28.64 | 286.4
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 10 | Each | 26.26 | 262.6
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 61.35 | 1227
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 30 | Each | 108.32 | 3249.6
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 313.09 | 3130.9
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 117.88 | 2357.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 20 | Each | 53.94 | 1078.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 46.63 | 466.3
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 181.48 | 1814.8
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 534 | 5340
0
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
0
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 10 | Each | 237 | 2370
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 10 | Each | 784 | 7840
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 150 | Point | 767.28 | 115092
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 848 | 16960
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 20 | Point | 1064.88 | 21297.6
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 380.78 | 19039
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 150 | Point | 675.32 | 101298
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 913.49 | 9134.9
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 777.84 | 7778.4
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 30 | Point | 350.64 | 10519.2
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 25 | Point | 339.31 | 8482.75
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 215 | Rft | 36.55 | 7858.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 28.85 | 4327.5
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 110 | Rft | 32.59 | 3584.9
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 325 | Rft | 44.48 | 14456
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.67 | 5500.5
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 155 | Rft | 35.02 | 5428.1
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 32.85 | 4927.5
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 250 | Rft | 35.42 | 8855
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 250 | Rft | 44.08 | 11020
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 38.02 | 5703
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 80 | Rft | 38.81 | 3104.8
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 60 | Rft | 56.69 | 3401.4
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 125 | Rft | 60.27 | 7533.75
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 72.27 | 18067.5
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 150 | Rft | 93.33 | 13999.5
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 90 | Rft | 131.03 | 11792.7
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 60 | Rft | 78.72 | 4723.2
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 40 | Rft | 105.71 | 4228.4
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 250 | Rft | 136.58 | 34145
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 350 | Each | 27.38 | 9583
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 50 | Each | 26.62 | 1331
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 30 | Each | 65.96 | 1978.8
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 20 | Each | 119.81 | 2396.2
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 20 | Each | 195.6 | 3912
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 20 | Each | 128.24 | 2564.8
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 150 | Each | 47.13 | 7069.5
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 20 | Each | 138.22 | 2764.4
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 15 | Each | 290.84 | 4362.6
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 10 | Each | 396.44 | 3964.4
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 15 | Each | 514.58 | 7718.7
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 10 | Each | 565.84 | 5658.4
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 6 | Each | 943.58 | 5661.48
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 5 | Each | 247.58 | 1237.9
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 15 | Each | 1803.45 | 27051.75
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 5 | Each | 4155.25 | 20776.25
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 2 | Each | 4911.5 | 9823
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 2 | Each | 2238.5 | 4477
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 25 | P/Sft | 2420 | 60500
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 5 | Each | 1765.5 | 8827.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 5 | Set | 220 | 1100
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 0 | Each | 2524.5 | 0
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 0 | Each | 7557 | 0
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 20 | Each | 2018 | 40360
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 20 | Each | 1897 | 37940
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 20 | Each | 572 | 11440
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 30 | Each | 376 | 11280
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 20 | Each | 359 | 7180
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 30 | Each | 277 | 8310
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 15 | Each | 589 | 8835
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 30 | Each | 2031 | 60930
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 20 | Each | 2088 | 41760
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1884 | 18840
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1866 | 9330
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1400 | 8400
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 8 | Each | 1286 | 10288
| LT CABLES |  |  |  | 0
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 100 | Rft | 217.8 | 21780
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 1500 | Cft | 3.63 | 5445
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 1 | Each | 8476 | 8476
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 1 | Each | 7947 | 7947
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 3 | Each | 3245 | 9735
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 120 | 100 Cft | 10063 | 12075.6
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 12 | Each | 65 | 780
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 80 | Rft | 93.32 | 7465.6
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 16 | Each | 389 | 6224
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 4 | Each | 571 | 2284
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 1268164.14

## SUKKUR CIRCLE ELECT.
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CIRCLE OFFICE AT SITE AREA SUKKUR
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 35 | Each | 109.34 | 3826.9
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 25 | Each | 28.04 | 701
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 45 | Each | 279.46 | 12575.7
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 20 | Each | 613.31 | 12266.2
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 661.38 | 3306.9
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 3823.88 | 7647.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 4693.56 | 9387.12
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 2033.56 | 4067.12
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 3563.51 | 3563.51
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 23.9 | 478
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 28.64 | 286.4
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 10 | Each | 26.26 | 262.6
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 61.35 | 1227
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 30 | Each | 108.32 | 3249.6
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 313.09 | 3130.9
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 117.88 | 2357.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 20 | Each | 53.94 | 1078.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 46.63 | 466.3
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 181.48 | 1814.8
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 534 | 5340
0
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
0
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 10 | Each | 237 | 2370
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 10 | Each | 784 | 7840
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 80 | Point | 767.28 | 61382.4
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 848 | 16960
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 20 | Point | 1064.88 | 21297.6
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 380.78 | 19039
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 20 | Point | 675.32 | 13506.4
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 5 | Point | 913.49 | 4567.45
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 777.84 | 7778.4
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 350.64 | 3506.4
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 20 | Point | 339.31 | 6786.2
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 36.55 | 5482.5
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 80 | Rft | 28.85 | 2308
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 70 | Rft | 32.59 | 2281.3
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 80 | Rft | 44.48 | 3558.4
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 80 | Rft | 36.67 | 2933.6
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 35.02 | 5253
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 50 | Rft | 32.85 | 1642.5
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 35.42 | 5313
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 44.08 | 6612
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 38.02 | 5703
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 80 | Rft | 38.81 | 3104.8
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 60 | Rft | 56.69 | 3401.4
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 125 | Rft | 60.27 | 7533.75
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 72.27 | 18067.5
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 150 | Rft | 93.33 | 13999.5
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 90 | Rft | 131.03 | 11792.7
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 60 | Rft | 78.72 | 4723.2
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 40 | Rft | 105.71 | 4228.4
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 250 | Rft | 136.58 | 34145
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 350 | Each | 27.38 | 9583
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 50 | Each | 26.62 | 1331
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 30 | Each | 65.96 | 1978.8
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 20 | Each | 119.81 | 2396.2
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 20 | Each | 195.6 | 3912
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 20 | Each | 128.24 | 2564.8
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 150 | Each | 47.13 | 7069.5
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 20 | Each | 138.22 | 2764.4
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 15 | Each | 290.84 | 4362.6
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 10 | Each | 396.44 | 3964.4
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 15 | Each | 514.58 | 7718.7
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 10 | Each | 565.84 | 5658.4
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 6 | Each | 943.58 | 5661.48
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 5 | Each | 247.58 | 1237.9
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 15 | Each | 1803.45 | 27051.75
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 5 | Each | 4155.25 | 20776.25
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 2 | Each | 4911.5 | 9823
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 2 | Each | 2238.5 | 4477
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 25 | P/Sft | 2420 | 60500
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 5 | Each | 1765.5 | 8827.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 5 | Set | 220 | 1100
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 0 | Each | 2524.5 | 0
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 0 | Each | 7557 | 0
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 20 | Each | 2018 | 40360
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 20 | Each | 1897 | 37940
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 20 | Each | 572 | 11440
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 30 | Each | 376 | 11280
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 20 | Each | 359 | 7180
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 30 | Each | 277 | 8310
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 15 | Each | 589 | 8835
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 10 | Each | 2031 | 20310
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 2088 | 20880
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1884 | 9420
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1866 | 9330
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1400 | 8400
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 8 | Each | 1286 | 10288
| LT CABLES |  |  |  | 0
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 100 | Rft | 217.8 | 21780
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 1500 | Cft | 3.63 | 5445
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 1 | Each | 8476 | 8476
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 1 | Each | 7947 | 7947
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 3 | Each | 3245 | 9735
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 120 | 100 Cft | 10063 | 12075.6
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 12 | Each | 65 | 780
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 80 | Rft | 93.32 | 7465.6
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 16 | Each | 389 | 6224
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 4 | Each | 571 | 2284
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 999014.62

## SUKKUR CITY DISP ELECT
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF CITY DISPENSARY SUKKUR
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 20 | Each | 109.34 | 2186.8
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 15 | Each | 28.04 | 420.6
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 20 | Each | 279.46 | 5589.2
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 613.31 | 3066.55
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 661.38 | 1322.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 1 | Each | 3823.88 | 3823.88
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 0 | Each | 4693.56 | 0
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 2033.56 | 2033.56
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 3563.51 | 3563.51
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 23.9 | 478
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 28.64 | 143.2
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 5 | Each | 26.26 | 131.3
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 61.35 | 613.5
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 15 | Each | 108.32 | 1624.8
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 313.09 | 1565.45
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 117.88 | 1178.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 5 | Each | 53.94 | 269.7
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 46.63 | 93.26
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 209.43 | 418.86
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 181.48 | 362.96
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 534 | 2670
0
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
0
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 5 | Each | 237 | 1185
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 0 | Each | 784 | 0
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 60 | Point | 767.28 | 46036.8
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 848 | 8480
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 1064.88 | 10648.8
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 30 | Point | 380.78 | 11423.4
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 5 | Point | 675.32 | 3376.6
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 5 | Point | 913.49 | 4567.45
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 5 | Point | 777.84 | 3889.2
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 5 | Point | 350.64 | 1753.2
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 20 | Point | 339.31 | 6786.2
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 40 | Rft | 36.55 | 1462
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 40 | Rft | 28.85 | 1154
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 30 | Rft | 32.59 | 977.7
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 60 | Rft | 44.48 | 2668.8
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 60 | Rft | 36.67 | 2200.2
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 35.02 | 5253
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 50 | Rft | 32.85 | 1642.5
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 35.42 | 4250.4
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 44.08 | 5289.6
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 125 | Rft | 38.02 | 4752.5
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 80 | Rft | 38.81 | 3104.8
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 60 | Rft | 56.69 | 3401.4
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 125 | Rft | 60.27 | 7533.75
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 72.27 | 18067.5
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 150 | Rft | 93.33 | 13999.5
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 90 | Rft | 131.03 | 11792.7
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 60 | Rft | 78.72 | 4723.2
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 0 | Rft | 105.71 | 0
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 0 | Rft | 78.81 | 0
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 0 | Rft | 124.82 | 0
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 0 | Rft | 136.58 | 0
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 25 | Each | 27.38 | 684.5
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 20 | Each | 26.62 | 532.4
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 10 | Each | 65.96 | 659.6
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 20 | Each | 119.81 | 2396.2
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 10 | Each | 195.6 | 1956
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 20 | Each | 128.24 | 2564.8
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 45 | Each | 47.13 | 2120.85
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 10 | Each | 290.84 | 2908.4
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 10 | Each | 396.44 | 3964.4
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 10 | Each | 514.58 | 5145.8
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 5 | Each | 565.84 | 2829.2
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 6 | Each | 943.58 | 5661.48
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 20 | Each | 50.65 | 1013
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 5 | Each | 247.58 | 1237.9
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 5 | Each | 1803.45 | 9017.25
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 3 | Each | 4155.25 | 12465.75
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 1 | Each | 4911.5 | 4911.5
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 2 | Each | 2238.5 | 4477
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 25 | P/Sft | 2420 | 60500
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 2 | Each | 1765.5 | 3531
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 2 | Set | 220 | 440
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 0 | Each | 2524.5 | 0
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 0 | Each | 7557 | 0
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 5 | Each | 2018 | 10090
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 5 | Each | 1897 | 9485
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 15 | Each | 572 | 8580
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 10 | Each | 376 | 3760
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 10 | Each | 359 | 3590
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 20 | Each | 277 | 5540
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 10 | Each | 589 | 5890
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 2 | Each | 2031 | 4062
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 2088 | 10440
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 4 | Each | 1884 | 7536
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 3 | Each | 1866 | 5598
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 2 | Each | 1400 | 2800
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1286 | 7716
| LT CABLES |  |  |  | 0
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 100 | Rft | 217.8 | 21780
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 1500 | Cft | 3.63 | 5445
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 0 | Each | 8476 | 0
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 0 | Each | 7947 | 0
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 2 | Each | 3245 | 6490
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 60 | 100 Cft | 10063 | 6037.8
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 9 | Each | 65 | 585
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 60 | Rft | 93.32 | 5599.2
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 8 | Each | 389 | 3112
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 2 | Each | 571 | 1142
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 609812.1

## Kotri Hospital Elect.
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (MAIN HOSPITAL )
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 65 | Each | 109.34 | 7107.1
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 65 | Each | 28.04 | 1822.6
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 45 | Each | 279.46 | 12575.7
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 1 | Each | 1438.51 | 1438.51
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 1 | Each | 4131.38 | 4131.38
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 5 | Each | 1293.88 | 6469.4
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 20 | Each | 613.31 | 12266.2
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 10 | Each | 661.38 | 6613.8
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 4 | Each | 3823.88 | 15295.52
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 1 | Each | 4693.56 | 4693.56
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 2033.56 | 4067.12
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 3563.51 | 7127.02
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 23.9 | 956
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 30 | Each | 28.64 | 859.2
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 36.55 | 731
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 20 | Each | 26.26 | 525.2
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 61.35 | 2454
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 108.32 | 4332.8
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 313.09 | 6261.8
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 117.88 | 2357.6
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 20 | Each | 53.94 | 1078.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 40 | Each | 46.63 | 1865.2
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 25 | Each | 181.48 | 4537
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 534 | 5340
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 16 | Each | 237 | 3792
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 10 | Each | 784 | 7840
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 767.28 | 38364
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 848 | 16960
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 20 | Point | 1064.88 | 21297.6
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 50 | Point | 380.78 | 19039
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 125 | Point | 675.32 | 84415
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 20 | Point | 913.49 | 18269.8
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 777.84 | 7778.4
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 350.64 | 7012.8
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 20 | Point | 339.31 | 6786.2
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 115 | Rft | 36.55 | 4203.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 75 | Rft | 28.85 | 2163.75
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 125 | Rft | 44.48 | 5560
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 125 | Rft | 36.67 | 4583.75
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 130 | Rft | 35.02 | 4552.6
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 32.85 | 4927.5
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 35.42 | 5313
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 350 | Rft | 44.08 | 15428
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 210 | Rft | 38.02 | 7984.2
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 125 | Rft | 38.81 | 4851.25
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 150 | Rft | 56.69 | 8503.5
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 235 | Rft | 60.27 | 14163.45
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 72.27 | 18067.5
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 120 | Rft | 93.33 | 11199.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 150 | Rft | 131.03 | 19654.5
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 150 | Rft | 78.72 | 11808
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 150 | Rft | 105.71 | 15856.5
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 250 | Rft | 136.58 | 34145
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 120 | Each | 27.38 | 3285.6
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 30 | Each | 26.62 | 798.6
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 25 | Each | 65.96 | 1649
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 25 | Each | 119.81 | 2995.25
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 20 | Each | 195.6 | 3912
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 20 | Each | 128.24 | 2564.8
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 175 | Each | 47.13 | 8247.75
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 20 | Each | 138.22 | 2764.4
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 10 | Each | 290.84 | 2908.4
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 20 | Each | 514.58 | 10291.6
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 20 | Each | 565.84 | 11316.8
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 30 | Each | 1803.45 | 54103.5
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 20 | Each | 4155.25 | 83105
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4911.5 | 19646
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 5 | Each | 2238.5 | 11192.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 25 | P/Sft | 2420 | 60500
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 3 | Each | 1765.5 | 5296.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 3 | Set | 220 | 660
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 0 | Each | 2524.5 | 0
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 0 | Each | 7557 | 0
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 25 | Each | 2018 | 50450
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 20 | Each | 1897 | 37940
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 20 | Each | 572 | 11440
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 100 | Each | 376 | 37600
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 20 | Each | 359 | 7180
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 60 | Each | 277 | 16620
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 15 | Each | 589 | 8835
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 40 | Each | 2031 | 81240
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 10 | Each | 7158 | 71580
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 20 | Each | 2088 | 41760
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1884 | 18840
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1866 | 9330
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1400 | 8400
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 1286 | 12860
| LT CABLES |  |  |  | 0
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 80 | Rft | 217.8 | 17424
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 60 | Rft | 332.75 | 19965
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 2650 | Cft | 3.63 | 9619.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 1 | Each | 8476 | 8476
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 1 | Each | 7947 | 7947
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 3 | Each | 3245 | 9735
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 120 | 100 Cft | 10063 | 12075.6
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 20 | Each | 65 | 1300
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 80 | Rft | 93.32 | 7465.6
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 16 | Each | 389 | 6224
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 4 | Each | 571 | 2284
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 1508040.29

## Kotri Hosp.Doctor's Res
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (DOCTOR'S RESIDENCE )
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 10 | Each | 109.34 | 1093.4
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 20 | Each | 28.04 | 560.8
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 25 | Each | 279.46 | 6986.5
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 613.31 | 3066.55
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 661.38 | 1322.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 3823.88 | 7647.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 0 | Each | 4693.56 | 0
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 2033.56 | 4067.12
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 0 | Each | 3563.51 | 0
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 25 | Each | 28.59 | 714.75
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 23.9 | 478
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 28.64 | 286.4
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 5 | Each | 26.26 | 131.3
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 61.35 | 613.5
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 108.32 | 1083.2
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 313.09 | 1565.45
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 117.88 | 1178.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 10 | Each | 53.94 | 539.4
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 46.63 | 233.15
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 181.48 | 907.4
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 534 | 2670
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 89 | 445
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 0 | Each | 237 | 0
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 0 | Each | 784 | 0
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 15 | Point | 767.28 | 11509.2
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 848 | 8480
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 18 | Point | 1064.88 | 19167.84
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 380.78 | 7615.6
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 10 | Point | 675.32 | 6753.2
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 5 | Point | 913.49 | 4567.45
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 777.84 | 7778.4
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 5 | Point | 350.64 | 1753.2
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 5 | Point | 339.31 | 1696.55
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 115 | Rft | 36.55 | 4203.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 25 | Rft | 28.85 | 721.25
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 60 | Rft | 44.48 | 2668.8
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 45 | Rft | 36.67 | 1650.15
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 45 | Rft | 35.02 | 1575.9
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 20 | Rft | 32.85 | 657
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 10 | Rft | 35.42 | 354.2
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 25 | Rft | 44.08 | 1102
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 20 | Rft | 38.02 | 760.4
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 38.81 | 1164.3
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 56.69 | 1700.7
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 20 | Rft | 60.27 | 1205.4
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 20 | Rft | 72.27 | 1445.4
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 20 | Rft | 93.33 | 1866.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 20 | Rft | 131.03 | 2620.6
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 20 | Rft | 78.72 | 1574.4
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 30 | Rft | 105.71 | 3171.3
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 20 | Rft | 78.81 | 1576.2
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 0 | Rft | 136.58 | 0
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 10 | Each | 27.38 | 273.8
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 5 | Each | 26.62 | 133.1
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 10 | Each | 65.96 | 659.6
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 15 | Each | 119.81 | 1797.15
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 10 | Each | 195.6 | 1956
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 10 | Each | 128.24 | 1282.4
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 85 | Each | 47.13 | 4006.05
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 15 | Each | 290.84 | 4362.6
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 25 | Each | 514.58 | 12864.5
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 20 | Each | 565.84 | 11316.8
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 4 | Each | 247.58 | 990.32
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 5 | Each | 1803.45 | 9017.25
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 2 | Each | 4155.25 | 8310.5
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 0 | Each | 4911.5 | 0
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 3 | Each | 2238.5 | 6715.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 20 | P/Sft | 2420 | 48400
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 2 | Each | 1765.5 | 3531
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 2 | Set | 220 | 440
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 0 | Each | 2524.5 | 0
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 0 | Each | 7557 | 0
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 4 | Each | 2018 | 8072
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 4 | Each | 1897 | 7588
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 6 | Each | 572 | 3432
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 6 | Each | 376 | 2256
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 8 | Each | 359 | 2872
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 8 | Each | 277 | 2216
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 8 | Each | 589 | 4712
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 0 | Each | 2031 | 0
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 2088 | 10440
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 4 | Each | 1884 | 7536
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 4 | Each | 1866 | 7464
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 2 | Each | 1400 | 2800
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1286 | 7716
LT CABLES
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 75 | Rft | 217.8 | 16335
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 0 | Job | 8358 | 0
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 160 | Cft | 3.63 | 580.8
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 0 | Each | 8476 | 0
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 0 | Each | 7947 | 0
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 2 | Each | 3245 | 6490
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 40 | 100 Cft | 10063 | 4025.2
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 8 | Each | 65 | 520
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 40 | Rft | 93.32 | 3732.8
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 8 | Each | 389 | 3112
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 2 | Each | 571 | 1142
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 506325.73

## Kotri Hosp.Para Med Res.
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI HOSPITAL AT SITE AREA KOTRI (PARA MEDICAL STAFF'S RESIDENCE )
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 10 | Each | 109.34 | 1093.4
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 20 | Each | 28.04 | 560.8
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 30 | Each | 279.46 | 8383.8
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 613.31 | 3066.55
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 661.38 | 1322.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 3823.88 | 7647.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 0 | Each | 4693.56 | 0
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 2033.56 | 4067.12
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 0 | Each | 3563.51 | 0
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 25 | Each | 28.59 | 714.75
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 23.9 | 478
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 28.64 | 286.4
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 5 | Each | 26.26 | 131.3
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 61.35 | 613.5
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 108.32 | 1083.2
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 313.09 | 1565.45
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 117.88 | 1178.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 10 | Each | 53.94 | 539.4
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 46.63 | 233.15
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 181.48 | 907.4
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 534 | 2670
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 89 | 445
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 0 | Each | 237 | 0
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 0 | Each | 784 | 0
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 15 | Point | 767.28 | 11509.2
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 848 | 8480
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 18 | Point | 1064.88 | 19167.84
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 380.78 | 7615.6
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 10 | Point | 675.32 | 6753.2
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 5 | Point | 913.49 | 4567.45
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 777.84 | 7778.4
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 5 | Point | 350.64 | 1753.2
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 5 | Point | 339.31 | 1696.55
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 115 | Rft | 36.55 | 4203.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 25 | Rft | 28.85 | 721.25
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 60 | Rft | 44.48 | 2668.8
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 45 | Rft | 36.67 | 1650.15
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 45 | Rft | 35.02 | 1575.9
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 20 | Rft | 32.85 | 657
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 10 | Rft | 35.42 | 354.2
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 25 | Rft | 44.08 | 1102
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 20 | Rft | 38.02 | 760.4
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 38.81 | 1164.3
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 30 | Rft | 56.69 | 1700.7
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 20 | Rft | 60.27 | 1205.4
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 20 | Rft | 72.27 | 1445.4
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 20 | Rft | 93.33 | 1866.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 20 | Rft | 131.03 | 2620.6
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 20 | Rft | 78.72 | 1574.4
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 30 | Rft | 105.71 | 3171.3
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 20 | Rft | 78.81 | 1576.2
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 0 | Rft | 136.58 | 0
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 10 | Each | 27.38 | 273.8
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 5 | Each | 26.62 | 133.1
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 10 | Each | 65.96 | 659.6
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 15 | Each | 119.81 | 1797.15
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 10 | Each | 195.6 | 1956
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 10 | Each | 128.24 | 1282.4
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 85 | Each | 47.13 | 4006.05
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 15 | Each | 290.84 | 4362.6
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 25 | Each | 514.58 | 12864.5
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 20 | Each | 565.84 | 11316.8
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 4 | Each | 247.58 | 990.32
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 5 | Each | 1803.45 | 9017.25
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 2 | Each | 4155.25 | 8310.5
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 0 | Each | 4911.5 | 0
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 3 | Each | 2238.5 | 6715.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 20 | P/Sft | 2420 | 48400
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 2 | Each | 1765.5 | 3531
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 2 | Set | 220 | 440
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 0 | Each | 2524.5 | 0
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 0 | Each | 7557 | 0
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 4 | Each | 2018 | 8072
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 4 | Each | 1897 | 7588
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 6 | Each | 572 | 3432
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 6 | Each | 376 | 2256
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 8 | Each | 359 | 2872
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 8 | Each | 277 | 2216
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 8 | Each | 589 | 4712
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 0 | Each | 2031 | 0
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 2088 | 10440
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 0 | Each | 1884 | 0
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 0 | Each | 1866 | 0
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 2 | Each | 1400 | 2800
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1286 | 7716
LT CABLES
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 75 | Rft | 217.8 | 16335
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 0 | Job | 8358 | 0
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 160 | Cft | 3.63 | 580.8
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 0 | Each | 8476 | 0
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 0 | Each | 7947 | 0
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 2 | Each | 3245 | 6490
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 40 | 100 Cft | 10063 | 4025.2
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 8 | Each | 65 | 520
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 40 | Rft | 93.32 | 3732.8
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 8 | Each | 389 | 3112
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 2 | Each | 571 | 1142
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 492723.03

## kOTRI CITY dISPENSARY
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF KOTRI CITY DISPENSARY KOTRI SINDH
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 20 | Each | 109.34 | 2186.8
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 15 | Each | 28.04 | 420.6
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 20 | Each | 279.46 | 5589.2
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 613.31 | 3066.55
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 661.38 | 1322.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 1 | Each | 3823.88 | 3823.88
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 0 | Each | 4693.56 | 0
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 2033.56 | 2033.56
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 3563.51 | 3563.51
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 28.59 | 571.8
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 23.9 | 478
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 28.64 | 143.2
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 5 | Each | 26.26 | 131.3
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 61.35 | 613.5
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 15 | Each | 108.32 | 1624.8
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 313.09 | 1565.45
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 117.88 | 1178.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 5 | Each | 53.94 | 269.7
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 46.63 | 93.26
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 209.43 | 418.86
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 181.48 | 362.96
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 534 | 2670
0
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
0
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 5 | Each | 237 | 1185
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 0 | Each | 784 | 0
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 60 | Point | 767.28 | 46036.8
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 848 | 8480
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 1064.88 | 10648.8
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 30 | Point | 380.78 | 11423.4
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 5 | Point | 675.32 | 3376.6
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 5 | Point | 913.49 | 4567.45
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 5 | Point | 777.84 | 3889.2
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 5 | Point | 350.64 | 1753.2
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 20 | Point | 339.31 | 6786.2
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 40 | Rft | 36.55 | 1462
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 40 | Rft | 28.85 | 1154
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 30 | Rft | 32.59 | 977.7
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 60 | Rft | 44.48 | 2668.8
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 60 | Rft | 36.67 | 2200.2
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 150 | Rft | 35.02 | 5253
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 50 | Rft | 32.85 | 1642.5
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 35.42 | 4250.4
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 44.08 | 5289.6
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 125 | Rft | 38.02 | 4752.5
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 80 | Rft | 38.81 | 3104.8
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 60 | Rft | 56.69 | 3401.4
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 125 | Rft | 60.27 | 7533.75
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 72.27 | 18067.5
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 150 | Rft | 93.33 | 13999.5
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 90 | Rft | 131.03 | 11792.7
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 60 | Rft | 78.72 | 4723.2
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 0 | Rft | 105.71 | 0
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 0 | Rft | 78.81 | 0
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 0 | Rft | 124.82 | 0
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 0 | Rft | 136.58 | 0
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 25 | Each | 27.38 | 684.5
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 20 | Each | 26.62 | 532.4
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 10 | Each | 65.96 | 659.6
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 20 | Each | 119.81 | 2396.2
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 10 | Each | 195.6 | 1956
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 20 | Each | 128.24 | 2564.8
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 45 | Each | 47.13 | 2120.85
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 10 | Each | 138.22 | 1382.2
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 10 | Each | 290.84 | 2908.4
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 10 | Each | 396.44 | 3964.4
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 10 | Each | 514.58 | 5145.8
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 5 | Each | 565.84 | 2829.2
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 6 | Each | 943.58 | 5661.48
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 20 | Each | 50.65 | 1013
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 5 | Each | 247.58 | 1237.9
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 5 | Each | 1803.45 | 9017.25
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 3 | Each | 4155.25 | 12465.75
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 1 | Each | 4911.5 | 4911.5
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 2 | Each | 2238.5 | 4477
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 25 | P/Sft | 2420 | 60500
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 2 | Each | 1765.5 | 3531
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 2 | Set | 220 | 440
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 0 | Each | 2524.5 | 0
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 0 | Each | 7557 | 0
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 5 | Each | 2018 | 10090
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 5 | Each | 1897 | 9485
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 15 | Each | 572 | 8580
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 10 | Each | 376 | 3760
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 10 | Each | 359 | 3590
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 20 | Each | 277 | 5540
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 10 | Each | 589 | 5890
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 2 | Each | 2031 | 4062
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 2088 | 10440
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 4 | Each | 1884 | 7536
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 3 | Each | 1866 | 5598
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 2 | Each | 1400 | 2800
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 6 | Each | 1286 | 7716
| LT CABLES |  |  |  | 0
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 100 | Rft | 217.8 | 21780
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 0 | Rft | 332.75 | 0
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 1500 | Cft | 3.63 | 5445
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 0 | Each | 8476 | 0
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 0 | Each | 7947 | 0
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 2 | Each | 3245 | 6490
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 60 | 100 Cft | 10063 | 6037.8
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 9 | Each | 65 | 585
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 60 | Rft | 93.32 | 5599.2
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 8 | Each | 389 | 3112
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 2 | Each | 571 | 1142
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 609812.1

## Med.centre at Tando Adam (Elec)
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI MEDICAL CENTRE TANDO ADAM
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 20 | Each | 109.34 | 2186.8
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 20 | Each | 28.04 | 560.8
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 30 | Each | 279.46 | 8383.8
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 613.31 | 3066.55
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 5 | Each | 661.38 | 3306.9
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 3823.88 | 7647.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 1 | Each | 4693.56 | 4693.56
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 2033.56 | 2033.56
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 3563.51 | 7127.02
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 16 | Each | 28.59 | 457.44
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 23.9 | 239
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 6 | Each | 28.64 | 171.84
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 0 | Each | 26.26 | 0
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 61.35 | 613.5
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 108.32 | 1083.2
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 313.09 | 3130.9
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 117.88 | 1178.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 10 | Each | 53.94 | 539.4
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 46.63 | 233.15
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 209.43 | 1047.15
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 5 | Each | 181.48 | 907.4
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 534 | 2670
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 5 | Each | 237 | 1185
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 0 | Each | 784 | 0
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 767.28 | 15345.6
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 848 | 8480
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 1064.88 | 10648.8
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 380.78 | 7615.6
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 20 | Point | 675.32 | 13506.4
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 913.49 | 9134.9
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 777.84 | 7778.4
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 350.64 | 7012.8
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 20 | Point | 339.31 | 6786.2
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 115 | Rft | 36.55 | 4203.25
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 75 | Rft | 28.85 | 2163.75
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 125 | Rft | 44.48 | 5560
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 125 | Rft | 36.67 | 4583.75
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 130 | Rft | 35.02 | 4552.6
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 32.85 | 4927.5
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 35.42 | 5313
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 350 | Rft | 44.08 | 15428
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 210 | Rft | 38.02 | 7984.2
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 125 | Rft | 38.81 | 4851.25
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 150 | Rft | 56.69 | 8503.5
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 235 | Rft | 60.27 | 14163.45
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 250 | Rft | 72.27 | 18067.5
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 120 | Rft | 93.33 | 11199.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 150 | Rft | 131.03 | 19654.5
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 150 | Rft | 78.72 | 11808
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 150 | Rft | 105.71 | 15856.5
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 124.82 | 6241
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 250 | Rft | 136.58 | 34145
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 20 | Each | 27.38 | 547.6
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 10 | Each | 26.62 | 266.2
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 20 | Each | 65.96 | 1319.2
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 20 | Each | 119.81 | 2396.2
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 10 | Each | 195.6 | 1956
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 10 | Each | 128.24 | 1282.4
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 55 | Each | 47.13 | 2592.15
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 20 | Each | 138.22 | 2764.4
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 10 | Each | 290.84 | 2908.4
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 10 | Each | 396.44 | 3964.4
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 10 | Each | 514.58 | 5145.8
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 10 | Each | 565.84 | 5658.4
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 30 | Each | 50.65 | 1519.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 5 | Each | 247.58 | 1237.9
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 10 | Each | 1803.45 | 18034.5
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 10 | Each | 4155.25 | 41552.5
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4911.5 | 19646
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 5 | Each | 2238.5 | 11192.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 25 | P/Sft | 2420 | 60500
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 3 | Each | 1765.5 | 5296.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 3 | Set | 220 | 660
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 0 | Each | 2524.5 | 0
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 0 | Each | 7557 | 0
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 15 | Each | 2018 | 30270
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 10 | Each | 1897 | 18970
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 10 | Each | 572 | 5720
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 20 | Each | 376 | 7520
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 10 | Each | 359 | 3590
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 30 | Each | 277 | 8310
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 15 | Each | 589 | 8835
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 20 | Each | 2031 | 40620
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 0 | Each | 7158 | 0
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 2088 | 20880
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1884 | 9420
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1866 | 9330
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 2 | Each | 1400 | 2800
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1286 | 6430
| LT CABLES |  |  |  | 0
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 60 | Rft | 217.8 | 13068
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 60 | Rft | 332.75 | 19965
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 2650 | Cft | 3.63 | 9619.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 0 | Each | 8476 | 0
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 0 | Each | 7947 | 0
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 2 | Each | 3245 | 6490
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 60 | 100 Cft | 10063 | 6037.8
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 12 | Each | 65 | 780
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 60 | Rft | 93.32 | 5599.2
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 10 | Each | 389 | 3890
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 2 | Each | 571 | 1142
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 914059.31

## Dispensary at Nooriabad (Elec)
SINDH EMPLOYEES SOCIAL SECURITY INSTITUTION ( SESSI )
ST-17 ,BLOCK -6 GULSHAN-E-IQBAL KARACHI
BILL OF QUANTITY FOR REPAIR & MAINTENANCE WORKS F/Y 2015 -2016
PROJECT :- R/M & RENNOVATION OF SESSI DESPENSARY AT SITE AREA NOORIABAD
SUB -HEAD (A ) ELECTRICAL WORKS
Schedule Item based on Pak PWD Schedule of Rates 2004
SH.Item/page | Description | Qty | Unit | Rate | Amount
MAINTENANCE WORK
CH-8/1-01 | Replacement of un- serviceable and burnt out 40/36 watts TLD Lamp with new one as per existing size and sample as required. | 20 | Each | 109.34 | 2186.8
CH-8/1-05 | Replacement of un- serviceable and burnt out 4-65 watts Starter with new one as per existing size and sample as required. | 20 | Each | 28.04 | 560.8
CH-8/1-11 | Replacement of un- serviceable and burnt out 20 to 24 watts PLC (Energy Saver) lamp with new one as per existing size and sample as required. | 30 | Each | 279.46 | 8383.8
CH-8/1-15 | Replacement of un- serviceable and burnt out 70 watts Sodium lamp with new one as per existing size and sample as required. | 0 | Each | 1438.51 | 0
CH-8/1-18 | Replacement of un- serviceable and burnt out 400 watts Sodium T lamp with new one as per existing size and sample as required. | 0 | Each | 4131.38 | 0
CH-8/1-36 | Replacement of un- serviceable and burnt out 20-40 watts Electronic Ballast with new one as per existing size and sample as required. | 0 | Each | 1293.88 | 0
CH-8/1-37 | Replacement of un- serviceable and burnt out 6 to 32 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 4 | Each | 613.31 | 2453.24
CH-8/1-38 | Replacement of un- serviceable and burnt out 50 to 63 Amps single pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 661.38 | 1322.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 15 to 60 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 2 | Each | 3823.88 | 7647.76
CH-8/1-42 | Replacement of un- serviceable and burnt out 75 to 100 Amps (Low breaking Capacity) Triple pole moulded case circuit breaker with new one as per existing size and sample as required. | 0 | Each | 4693.56 | 0
CH-8/1-76 | Replacement of un- serviceable and burnt out 60 Amps Triple Pole Iron Clad Main Switch on existing all kinds of board with new one as per existing size and sample as required. | 2 | Each | 2033.56 | 4067.12
CH-8/1-87 | Replacement of un- serviceable and burnt out 60 Amps 4 Pole change over Switch on existing all kinds of board with new one as per existing size and sample as required. | 1 | Each | 3563.51 | 3563.51
CH-8 /1-104 | Replacement of un- serviceable and burnt 6/10 Amps S.P Piano switch with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 28.59 | 285.9
CH-8 /1-105 | Replacement of un- serviceable and burnt 6/10 Amps S.P Two Pin Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 23.9 | 239
CH-8 /1-106 | Replacement of un- serviceable and burnt 6/10 Amps S.P bell Push with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 28.64 | 286.4
CH-8 /1-107 | Replacement of un- serviceable and burnt TV/Telephone Piano Socket with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 36.55 | 365.5
CH-8 /1-108 | Replacement of un- serviceable and burnt 6 amps Bed Switch with new one of all kinds as per existing size and sample as required. | 0 | Each | 26.26 | 0
CH-8 /1-109 | Replacement of un- serviceable and burnt out 6 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 61.35 | 1227
CH-8 /1-109 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 108.32 | 2166.4
CH-8 /1-115 | Replacement of un- serviceable and burnt out 20 Amps 3 Pin Porcelain base Combine Switch Socket unit (universal) Piano with new one of all kinds on existing board as per existing size and sample as required. | 20 | Each | 313.09 | 6261.8
CH-8 /1-116 | Replacement of un- serviceable and burnt out flush type piano Fan Dimmer with new one of all kinds on existing board as per existing size and sample as required. | 10 | Each | 117.88 | 1178.8
CH-8 /1-119 | Replacement of un- serviceable and burnt out flush type 20 Amps three pin shoe with new one as per existing size and sample as required. | 10 | Each | 53.94 | 539.4
CH-8 /1-119 | Replacement of un- serviceable and burnt out 10 Amps S.P Switch (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 46.63 | 93.26
CH-8 /1-119 | Replacement of un- serviceable and burnt out Click type Fan dimmer S.P (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 209.43 | 418.86
CH-8 /1-133 | Replacement of un- serviceable and burnt out 10 Amps Universal Scoko Socket (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 181.48 | 362.96
CH-8 /1-134 | Replacement of un- serviceable up to three lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 71.3 | 142.6
CH-8 /1-135 | Replacement of un- serviceable up to six lvory gang plate (Switch Kid) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 74.59 | 149.18
CH-8 /1-136 | Replacement of un- serviceable 10 Amps S.P Switch with one gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 133.16 | 266.32
CH-8 /1-138 | Replacement of un- serviceable 10 Amps S.P Switch with Three gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 314.05 | 628.1
CH-8 /1-141 | Replacement of un- serviceable 10 Amps S.P Switch with six gang plate (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 610.06 | 1220.12
CH-8 /1-146 | Replacement of un- serviceable and burnt out 15 Amps three pin universal Power Plug S.P (Clipsal) with new one of all kinds on existing board as per existing size and sample as required. | 2 | Each | 421.58 | 843.16
CH-8 /1-156 | Replacement of un- serviceable and burnt out 15 Amps 3 Pin Plug Shoe (Clipsal) with new one as per existing size and sample as required. | 2 | Each | 189.15 | 378.3
CH-8 /2-05 | Rewinding of burnt out A.C Ceiling Fan all kind sweep with suitable size of winding wire I/c varnishing /backing and testing on load complete in all respect i/c cartage and fixing charges as required. | 5 | Each | 534 | 2670
CH-8 /2-15 | Replacement of u/s and b/o Fan Capacitor 3.5 Mfd for all sweep suitable for 220 volts A.C supply complete in all respect i/c cartage and fixing charges as required. | 10 | Each | 89 | 890
CH-8 /3-05 | Spray painting after the Dismantling and re erecting of Ceiling fans/bracket fan/pedestal fan all kinds sweep complete with blades, down rod, canopy, including scraping the old paint and painting with two coats of superior white quality synthetic paint with golden lining and also replacement of worn out screw ,nut,split pin,etc as required. | 5 | Each | 237 | 1185
CH-8 /3-06 | Hand Painting of Steel Tubular pole of all size and type including cross arm,etc with fine coat of anti corrosive under coating and two coats of superior quality Silver or enamel paint as required. | 0 | Each | 784 | 0
WIRING FOR LIGHTS & FANS
CH-2 /2-01 | Wiring for light fan, or call bell point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 767.28 | 15345.6
CH-2 /2-03 | Wiring for two way light point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 848 | 8480
CH-2 /2-03 | Wiring for Call bell point point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 1064.88 | 10648.8
CH-2 /2-04 | Wiring for Plug point with (3/.029") PVC insulated wire in PVC cable duct fitted on surface, including 1mm², single core PVC insulated wire as ECC as required. | 20 | Point | 380.78 | 7615.6
0
CH-2 /4-01 | Wiring for light, fan or call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4") dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required. | 20 | Point | 675.32 | 13506.4
CH-2 /4-02 | Wiring for call bell point with (3/.029") PVC insulated wire in 20 mm², (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm² single core PVC insulated wire as ECC as required.(use when Push button out side the premises) | 10 | Point | 913.49 | 9134.9
CH-2 /4-03 | Wiring for two way light point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 777.84 | 7778.4
CH-2 /4-04 | Wiring for plug point with (3/.029") PVC insulated wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column, roof , including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 350.64 | 3506.4
0
CH-2 /8-01 | Wiring for light or fan point with (3/.029") PVC insulated wire in all kind of existing conduit or cable duct including 1 mm², single core PVC insulated wire as ECC as required. | 10 | Point | 339.31 | 3393.1
CH-2 /8-01 | Wiring for plug point with (3/.029") PVC insulated wire in all kinds of existing conduit or cable duct including 1mm², single core PVC insulated wire as ECC as required. | 10 | Point | 182.05 | 1820.5
CH-2 /20-03 | Wiring for sub-main with 2x 7/.029", 250/440 volts grade, PVC insulated wire single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 65 | Rft | 36.55 | 2375.75
CH-2 /20-01 | Wiring for sub-main with 2x 3/.029" PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 25 | Rft | 28.85 | 721.25
CH-2 /20-02 | Wiring for sub-main with 2x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")diaPVC conduit fitted on surface as required. | 60 | Rft | 32.59 | 1955.4
CH-2 /21-03 | Wiring for sub-main with 3x 7/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required | 85 | Rft | 44.48 | 3780.8
CH-2 /21-02 | Wiring for sub-main with 3x 3/.036", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 65 | Rft | 36.67 | 2383.55
CH-2 /21-01 | Wiring for sub-main with 3x 3/.029", PVC insulated wire 250/440 volts grade, single core copper conductor wire in 20 mm (3/4")dia PVC conduit fitted on surface as required. | 130 | Rft | 35.02 | 4552.6
CH-2 /39-01 | Wiring for sub-main with 2x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 150 | Rft | 32.85 | 4927.5
CH-2 /39-02 | Wiring for sub-main with 2x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 120 | Rft | 35.42 | 4250.4
CH-2 /39-03 | Wiring for sub-main with 2x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 250 | Rft | 44.08 | 11020
CH-2 /40-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc as required. | 85 | Rft | 38.02 | 3231.7
CH-2 /42-01 | Wiring for sub-main with 3x 1.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1mm² PVC insulated wire single core wire as ECC as required. | 85 | Rft | 38.81 | 3298.85
CH-2 /42-02 | Wiring for sub-main with 3x 2.5 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 20 mm (3/4")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 85 | Rft | 56.69 | 4818.65
CH-2 /42-03 | Wiring for sub-main with 3x 4 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 1.5 mm² PVC insulated wire single core wire as ECC as required. | 120 | Rft | 60.27 | 7232.4
CH-2 /42-04 | Wiring for sub-main with 3x 6 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 120 | Rft | 72.27 | 8672.4
CH-2 /42-05 | Wiring for sub-main with 3x 10 mm², PVC insulated wire 300/500 volts grade, single core, stranded copper conductor wire in 25 mm (1") diaPVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECCas required. | 120 | Rft | 93.33 | 11199.6
CH-2 /42-05 | Wiring for sub-main with 3x 16 mm², PVC insulated wire 450/750 volts grade, single core, stranded copper conductor wire in 30 mm (1¼")dia PVC conduit recessed in the wall, column and roof etc including 2.5 mm² PVC insulated wire single core wire as ECC as required. | 150 | Rft | 131.03 | 19654.5
CH-2 /53-04 | Wiring for sub-main with 3 core, 6 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 50 | Rft | 78.72 | 3936
CH-2 /53-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 33x33 mm PVC cable duct fitted on surface as required. | 0 | Rft | 105.71 | 0
CH-2 /58-03 | Wiring for sub-main with 3 core, 4 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 1.5mm single core PVC insulated wire as ECC in 25 mm (1") dia high pressure ' D' class uPVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 50 | Rft | 78.81 | 3940.5
CH-2 /58-05 | Wiring for sub-main with 3 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable i/c 2.5mm single core PVC insulated wire as ECC in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter as per Pak. P.W.D Specification as required. | 0 | Rft | 124.82 | 0
CH-2 /58-05 | Wiring for sub-main with 4 core, 10 mm², stranded copper conductor, PVC insulated & PVC sheathed cable in 30mm (1¼") dia high pressure ' D' class PVC conduit buried in ordinary soil at the depth of 0.5 meter including 4 mm² PVC insulated wire single core wire as ECC as per Pak. P.W.D Specifications as required. | 0 | Rft | 136.58 | 0
SWITCHES & BOARDS
CH-2 /69-01 | Providing & fixing, 6/10 Amps, flush type SP piano switch fitted on given sheet or all kind of board I/c connection as required. | 20 | Each | 27.38 | 547.6
CH-2 /69-03 | Providing & fixing, 6/10 Amps, flush type 2-pin piano socket fitted on given sheet or all kind of board including connection as required. | 10 | Each | 26.62 | 266.2
CH-2 /69-05 | Providing & fixing flush type, 6 Amps, 3-pin combine switch & socket unit (Universal) fitted on existing/given all kind of sheet or board sheet including connection as required. | 25 | Each | 65.96 | 1649
CH-2 /69-08 | Providing & fixing flush type, 15 Amps, 3-pin combine switch & socket unit (Power plug) fitted on existing/given all kinds of sheet or boards including connection as required. | 25 | Each | 119.81 | 2995.25
CH-2 /69-09 | Providing & fixing flush type, 20Amps, Porcelain base 3-pin combine switch & socket unit, fitted on existing/ given all kinds of sheet or boards including connection as required. | 20 | Each | 195.6 | 3912
CH-2 /69-10 | Providing & fixing flush type, Piano Fan Dimmer for all sweep fans , fitted on existing/given sheet or board including connection as required. | 20 | Each | 128.24 | 2564.8
CH-2 /75-01 | Providing & fixing 6 Amps plastic batten/Angle holder on PVC Round block/Round Cover fitted on surface including connection as required. | 150 | Each | 47.13 | 7069.5
CH-2 /74-01 | Providing & fixing 10 Amps Polycarbonate flame retardant S.P switch with fancy required gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E31-36/1/2A Clipsal make) | 20 | Each | 138.22 | 2764.4
CH-2 /74-02 | Providing & fixing 10 Amps Polycarbonate flame retardant Two way switch with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31/2/3A Clipsal make) | 10 | Each | 290.84 | 2908.4
CH-2 /74-03 | Providing & fixing 10 Amps Polycarbonate flame retardant Bell Push with fancy gang plate fixed on die fabricated, powder coated, metal board recessed in wall or column including connection as required. (E31MBPR Clipsal make) | 10 | Each | 397.54 | 3975.4
CH-2 /74-04 | Providing & fixing 10 Amps Polycarbonate flame retardant 2-Pin switch socket unit ( Universal) with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.(E15U Clipsal make) | 20 | Each | 396.44 | 7928.8
CH-2 /74-06 | Providing & fixing 15 Amps Polycarbonate flame retardant 3-Pin switch socket unit with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required.( Clipsal make) | 20 | Each | 514.58 | 10291.6
CH-2 /74-06 | Providing & fixing Polycarbonate flame retardant Telephone socket 4 contact single 2 line with fancy gang plate fixed on die fabricated, powder coated metal board recessed in wall or column including connection as required. (E31RJ64SM Clipsal make) | 20 | Each | 565.84 | 11316.8
CH-2 /74-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (E32V400F Clipsal make) | 20 | Each | 943.58 | 18871.6
CH-2 /75-04 | Providing & fixing 6 Amps plastic ceiling rose on PVC Round block/Round Cover fitted on surface including connection as required. | 50 | Each | 50.65 | 2532.5
CH-2 /75-07 | Providing & fixing Ding Dong/ Musical bell with magnetic, mechanical mechanism in Plastic body with metallic base on wooden block fitted on surface including connection as required. | 10 | Each | 247.58 | 2475.8
DISTRIBUTION BOARDS
CH-2 /82-01 | Providing & fixing 6 to 32 Amps, DP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 30 | Each | 1803.45 | 54103.5
CH-2 /82-02 | Providing & fixing 15 to 60 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 20 | Each | 4155.25 | 83105
CH-2 /82-03 | Providing & fixing 75 to100 Amps,(Low Breaking Capacity) TP MCCB fixed on metal board recessed in the wall duly covered with fiber sheet, I/c inter-connection as required. | 4 | Each | 4911.5 | 19646
CH-2 /79-01 | Providing & fixing rotary type, 32 Amps, 3 Phase, Phase selector switch fitted on all kind of existing board including incoming & outgoing connection as required. | 5 | Each | 2238.5 | 11192.5
CH-2 /83-01 | Providing & fixing Cubical type metal sheet Distribution board with locking arrangment as per drawing ,vermin protected duly powder coated paint i/c all fastening material including wiring with suitable gauge PVC x PVC wire complete as required. | 25 | P/Sft | 2420 | 60500
CH-2 /83-02 | Providing & fixing cubical type metal sheet vermin protected LT pannel board as per drawing with locking arragement duly powder coated I/c all fastening devices and electrical wire/ leads for internal connection complete as required. | 20 | P/Sft | 4372.5 | 87450
CH-2 /84-05 | Providing & fixing 10 to 60 Amps, 4 pole, three phase bus bar strip set (Standred size) fitted in suitable size metallic sheet steel box with hinged type front door duly painted and fixed on existing board I/c connection as required. | 3 | Each | 1765.5 | 5296.5
CH-2 /86-01 | Providing & fixing pilot lamp set fitted on existing board I/c connection as required. | 3 | Set | 220 | 660
CH-2 /87-01 | Providing & fixing single phase 10 to 40 Amps, 220/230 volts energy meter fitted on existing board I/c connection as required.( Syed Brother, PEL) | 0 | Each | 2524.5 | 0
CH-2 /87-02 | Providing & fixing Three phase 15 to 90 Amps, 400/440 volts energy meter fitted on existing board I/c connection as required. ( Syed Brother, PEL) | 0 | Each | 7557 | 0
LIGHT FIXTURES & ILLUMANIRES
CH-2 /88-51 | Providing & fixing basic batten, surface type, fitting complete with TL'D 2x36W white day light lamp, starter, electro magnetic ballast & capacitor as Philips Cat. (TMS-015/236) | 15 | Each | 2018 | 30270
CH-2 /88-55 | Providing & fixing basic batten, surface type, fitting complete with prismatic diffuser, TL'D 1x36W white day light lamp & electro magnetic ballast as Philips Cat (GMP-015/136) | 10 | Each | 1897 | 18970
CH-2 /88-58 | Providing & fixing Philips strip light Putty fitting complete with TL' D 1x36 watts white day lamp starter and electro magnetic ballast complete as required Philips (Cat No. P1-36) | 10 | Each | 572 | 5720
CH-2 /98-01 | Providing and fixing Putty fitting 4ft. size (Paklite PL40SL) complete with 1x40W/ 36W white tube lamp and starter as required. | 20 | Each | 376 | 7520
CH-2 /98-02 | Providing and fixing Putty fitting 2ft. size (Paklite PL20SL) complete with 1x20W/ 18W white tube lamp and starter as required. | 20 | Each | 359 | 7180
CH-2 /104-10 | Providing & fixing 6" dia Opel glass globe with aluminim gallary & brass holder I/c 11 watts ENERGY SAVER & connection as required | 30 | Each | 277 | 8310
CH-2 /104-05 | Providing & fixing fancy type, metalic powder coated, mirror light fitting, complete with 2 brass holders & candle lamp fitted on wooden block, as approved by the Engineer in-charge I/c connection | 10 | Each | 589 | 5890
CH-2 /100-02 | Providing and fixing Recessed ceiling lumnaire with high glass aluminium louvers (Paklite LQ420SV) complete with 4x20W/ 18W white tube lamp starter and capacitor as required. | 10 | Each | 2031 | 20310
CH-2 /102-03 | Providing and fixing Road light with bowel choke 150W (Paklite SN 150) complete with 1x150W sodium lamp and ignator as required. | 10 | Each | 7158 | 71580
FANS
CH-2 /106-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, strandard length of down rod including connection with 14.0076" flexable wire complete as required. (without regulator) Millat/Pak/Asia/ Younas/Climax/ Royal. | 10 | Each | 2088 | 20880
CH-2 /107-03 | Providing & installing 45 Cm (18") sweep wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1884 | 9420
CH-2 /108-01 | Providing & installing 35 Cm (14") sweep Plastic body Louvre wall bracket fan complete with blades, regulator & moveing grill with motor, fitted on wall or column with GI clip including connection with 14.0076" flexible wire complete as required. Millat/Pak/Asia/ Younas/Climax/ Royal. | 3 | Each | 1866 | 5598
CH-2 /109-02 | Providing & installing 30 Cm (12") sweep, mettalic body Exhaust fan complete with blades, motor, etc fitted in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 3 | Each | 1400 | 4200
CH-2 /110-01 | Providing & installing 20 Cm (8") sweep, Plastic body Exhaust fan complete with blades, motor, etc fixed in existing hole including connection with 14/.0076" flexable wire complete as required Millat/Pak/Asia/ Younas/Climax/ Royal. | 5 | Each | 1286 | 6430
| LT CABLES |  |  |  | 0
CH-3 /2-02 | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 45 | Rft | 217.8 | 9801
CH-3 /2-02 | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , armoured underground, L.T cable buried in the ground dully covered with sand and warning cable tiles as per Pak. P.W.D specification as required. | 45 | Rft | 332.75 | 14973.75
CH-3 /9-01 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) i/c fixing of 8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | 1 | Job | 8358 | 8358
CH-3 /10-05 | Excavation in all kind of Murum soil,hard,average or soft including lift up to 5ft and filling excavated earth including ,breaking clods,dressing ,watering, consolidation and ramming in layers to full compaction i/c disposal of surplus us excavated stuff as directed. | 2650 | Cft | 3.63 | 9619.5
PUMPS & FITTINGS
CH-5 /10-02 | Providing & fixing reciprocating pump (Donkey pump) 1HP having suction & discharge 1”x1” complete with motor mounted on a frame fixed as approved . | 1 | Each | 8566 | 8566
CH-5 /11-01 | Providing & fixing mono block pumping set complete with 1HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1”x1” as approved . | 1 | Each | 6533 | 6533
CH-5 /11-02 | Providing & fixing mono block pumping set complete with 2HP pump 2900 RPM complete with AC 220V single phase motor on a common base plate having suction & discharge 1- ½ ” x1- ½ ” as approved . | 1 | Each | 8476 | 8476
CH-5 /11-02 | Providing & fixing centrifugal pumping set complete with AC 1 HP 2900 RPM 220V 50 cycle motor with centrifugal pump JD/B model having suction & discharge 1” x 1 ” coupled on a common base plate as approved . | 0 | Each | 7947 | 0
CH-5 /15-01 | Providing & fixing Direct on line starter suitable for single phase 220 volts 50 cycle supply suitable up to 2 H.P TRIPPING RATING 3/10 Amps (Imported) on a Prepared board | 3 | Each | 3245 | 9735
CH-5 /1-01 | Providing & laying in situ 1:2:4 cement concrete using screen graded bajri in foundation and plinth i/c form work, rodding, compacting, curing etc. | 60 | 100 Cft | 10063 | 6037.8
CH-5 /3-02 | Providing & fixing foundation bolt and nuts 5/8 x12” Size with suitable steel base plate for pumping set or For other similar purpose as required. | 20 | Each | 65 | 1300
CH-5 /5-03 | Providing & fixing G.I pipe 1” dia medium gauge with special such as flanges, bend,Tee, union and socket etc for suction and delivery line etc i/c painting Two coats with white zinc paint with pigment to match the colour of other components as required. | 80 | Rft | 93.32 | 7465.6
CH-5 /6-05 | Providing & fixing brass gate valve 1” dia handle type imported make . | 16 | Each | 389 | 6224
CH-5 /7-01 | Providing & fixing 1” dia brass foot valve complete with kit local make . | 4 | Each | 571 | 2284
| ESTIMATED COST AS PER PAK PWD SCH 2004 |  |  |  | 960840.2