## Machinery
BILL OF QUANTITIES
(A) Description and rate of Items based on Composite Schedule of Rates.
Name of Work |  | SUPPLYING, INSTALLING AND TESTING PUMPING MACHINERY 10 BHP (2 SETS) & DIESEL ENGINE 16 BHP (2 SETS) I/C SUCTION & DELIVERY FOR REHABILITATION OF RURAL DRAINAGE SCHEME ALLAH BUX KUBBER TALUKA KAZI AHMED DISTRICT SHAHEED BENAZIR ABAD
Item No. | Description of item to be executed at site | [6 empty] | Unit | Quantity | Rate | Amount in Rupees
1 | C.I Reflex valve heavy pattern (Test pressure) 21 kg per sq: or 300 Lbs:/ Sq: inch (SMI No. 6 (b) P-12)
[7 empty] | 3" dia | Each | 2 | 1543.75 | 3087.5
2 | C.I Sluice valve heavy pattern (Test pressure) 21 kg per sq: or 300 Lbs:/ Sq: inch (SMI No. 2 (b) P-12)
[7 empty] | 3" dia | Each | 2 | 4290 | 8580
3 | Manufacturing installing M.S Pipe 3" & 4" made out M.S sheet 3/16” (4.8 mm thick) i/c cutting folding proper curvature shape i/c welding etc complete (R.A approved Based on Schedule rates)
[7 empty] | 3" dia | P: Rft: | 20 | 385.89 | 7717.8
4 | Providing, Laying & Fixing in trench i/c fitting, jointing & testing etc complete in all respect the high Density Polyethylene P.E pipes (HDPE-100) for W/S confirming ISO 4427/DIN8074 /8075 B.S 3580 & PSI 3051 (PHSI No. F (i) P-25)
(90 mm)
|  | For suction & delivery |  |  |  |  | 3" dia | P: Rft: | 35 | 178 | 6230
5 | Manufacturing installing M.S Flanged 3/8” (12 mm thick) M.S sheet of required size drilling holes i/c cutting bending to correct shape welding etc complete (R.A approved Based on Schedule rates)
[7 empty] | 3" dia | Each | 14 | 500.89 | 7012.46
6 | C.I Foot valve heavy pattern with cone type gate (Imported) (SMI No. 4 P-12)
[7 empty] | 3" dia | Each | 2 | 731.25 | 1462.5
7 | C.I Bend with flanged and with holes i/c turning and facing of flanges for all sizes (PHSI No. 8 P-12)
[6 empty] | Bend 90 3" dia |  | P: Kg | 33.4 | 120 | 4008
8 | C.I Tee flanged and with holes i/c turning and facing of flanges for all size (PHSI No. 12 P-13)
[7 empty] | 3" dia | P: Kg | 11.45 | 120 | 1374
9 | C.I Tappers flat bottomed or central tapper flanged ends with hole i/c turning & fixing for all sizes (SMI No. 9 P-12)
[5 empty] | Reducer 2 1/2" x 3" |  |  | P: Kg | 10.5 | 120 | 1260
Item No. | Description of item to be executed at site | [6 empty] | Unit | Quantity | Rate | Amount in Rupees
10 | But fusion Joint (PHS Mat: No. 1 P-21)
[7 empty] | 3" dia | Each | 14 | 600 | 8400
11 | Jointing C.I.M.S Flanged pipe and specials flanged and inside a trenches nuts and bolts with washer etc and other is required for joining and testing joints to the specified pressure etc complete (PHSI No.1 P-40)
[7 empty] | 3" dia | P: Joint | 16 | 499 | 7984
[10 empty] | TOTAL | 57116.26
|  | 57116.26 |  | x | 2 | = | 114232.52
| TOTAL AMOUNT |  | Rs. | 114233
| TOTAL (a) |  | Rs. | 114233
--------- | % above/ below on the rates of CSR. |  |  |  |  | Amount to be added/ deducted on the basis of
[6 empty] | of premium quoted |  |  | Total (b) | __________________
Total (A) = a + b in words & figures
|  |  | CONTRACTOR |  |  |  |  | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD

## Machinery (2)
BILL OF QUANTITIES
(B) Description and rate of Items based on Market (Offered rates)
Item No. | Description of item to be executed at site |  |  | Unit | Quantity | Rate | Amount in Rupees
1 | Supplying & installing in position i/c transportation to site of work @ Village Allah Bux Kubber electric pumping set consisting of A.C electric motor 10 BHP Siemens 3 Phase 50 cycle 400/420 volts of 1450 RPM made type (ILA4-130-4AA-60) coupled with KSB non-clogging pump type KWPZ (65-315) size 3“ x 2 1/2” mounted on common steel frame or base plate capable of discharge 370 gpm against the head of 40 ft: i/c installing of pumping set on cement concrete foundation Ratio (1:2:4) and C.C Ratio (1:4:8) with ballast with M.S nuts and bolts of 5/8” dia to be embedded in C.C foundation i/c providing and fixing automatic start delta starter Type (MCU) i/c providing & fixing prepared board iron (clad) triple pole and neutral switch fuse with requireable type fuse link carrier 500 volts and 0-50 ampars installed on metaled board i/c providing internal electric wiring for main switch with 3-7/0.52 (10mm) PVC insulated wire 660 volts grade in 25 mm (1”) PVC conduit on surface as required i/c providing and fixing earthing with set with 0.6m x 0.6m x 6.3 mm (2 x 2 x ½ “) G.I plate buried in ground at a depth of 3.7 m (12 ft:) for base plate & testing of the pumping set against the required head of 72 hours etc complete (R.A attached). |  |  | P:Set | 2
2 | Flange Adopter (M.R)
|  |  | 3" dia | Each | 14
TOTAL
| TOTAL AMOUNT | Rs.
| TOTAL (B) | Rs.
Total (B) in words & figures
|  | CONTRACTOR |  | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD

## Machinery (3)
BILL OF QUANTITIES
(B) Description and rate of Items based on Market (Offered rates)
PART-B |  | DIESEL ENGINE 16 BHP (2 SETS)
Item No. | Description of item to be executed at site |  |  | Unit | Quantity | Rate | Amount in Rupees
1 | Supplying & installing in position i/c transportation to site of work @ Village Allah Bux Kubber Diesel Engine 16 BHP (Golden) type (GD-1100) coupled with KSB non-clogging pump type (65-315) size 3“ x 2 1/2” mounted on common steel frame or base plate capable of discharge 370 gpm against the head of 40 ft: i/c installing of pumping set on cement concrete foundation Ratio (1:2:4) and C.C Ratio (1:4:8) with ballast with M.S nuts and bolts of 5/8” dia to be embedded in C.C foundation & testing of the pumping set against the required head of 72 hours etc complete (R.A attached).
|  |  |  | P: Set | 2
TOTAL
| TOTAL AMOUNT |  | Rs.
| TOTAL (B) |  | Rs.
Total (B) in words & figures
|  |  | CONTRACTOR | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD