## Part-A
BILL OF QUANTITIES
Name of Work:- |  | Supplying and installing Pumping Machinery and P.L.J and testing Rising Main 6" Dia for Pir Muhallah Urban Drainage Scheme Bhitshah Taluka Hala District Matiari.
Part (A) Pumping Machinery
S# | (A) Description and rate of Items based on Composite Schedule of Rates.
Item No. | Quantities | Descripition of item to be executed as site | RATE | Unit | Amount in Rupees
1 | 25.29 | C.I bend with flange ends with holes i/c tuning & facing of flangs for all size (PHSMI.No.8.P-11) | 120 | P.Kg | 3035
2 | 1 | Foot wall valve heavy pattern with cone type gate(imported) (PHSMI.No.4.P-11) | 731.25 | Each | 731
3 | 1 | Sluice valve heavy pattern tested pressure 21 kg/sq.cm or.300lbs)(imported) (PHSMI.No.2.P-9) | 4290 | Each | 4290
4 | 1 | Reflex valve heavy pattern tested pressure 21 kg/sq.cm or.300lbs)(imported) (PHSMI.No.6.P-10) | 1543.75 | Each | 1544
5 | 8 | Jointing C.I /MS flanged pipe and special flanged inside trenchis i/c supplying rubber paking of required thicknes nuts & bolts with washer etc and other tool required for jointing and testing the joint to the specified pressure etc complete(PHSMI.No.1.P-35) | 499 | P.J | 3992
|  |  | Total |  | 13592
_________% above / below on the rates of CSR _____________/- |  |  | Amount to be added /deducted on the basis of premium quoted TOTAL
Total (A) = in words & figures :_____________________________________________________________________
____________________________________________________________________________________________
EXECUTIVE ENGINEER
| Contractor |  | BUILDINGS DIVISION
Note:- Any omissionerror if occurs will be corrected. |  |  | MATIARI
BILL OF QUANTITIES
Name of Work:- |  | Supplying and installing Pumping Machinery and P.L.J and testing Rising Main 6" Dia for Pir Muhallah Urban Drainage Scheme Bhitshah Taluka Hala District Matiari.
Part (A) Pumping Machinery
S# | (B) Description and rate of Items based on Non Schedule Market Offer of Rates.
Item No. | Quantities | Descripition of item to be executed as site | RATE | Unit | Amount in Rupees
1 | 1 | Providing and installing in position i/c transportation to site of work Urban Drainage Scheme Pir Muhallah Bhitshah electric pumping set consisting of A.C.electric motor 7.50 BHP 3 phase 50 cycles 400/420 volts 1450 RPM (Siemens) frame size 132 M coupled with non closing pump KSB type KWP (65 -315 ) size 3" X 2.5" mounted on commen steel frame base plate capable discharge of 200 GPM aganist the Head of 50ft i/c installing of pumping set on C.C foundation ratio 1:2:4 with MS Nutts and Bolts of 5/2" dia to be embeded in C.C foundation i/c P/F on prepared board automatic MCU (Schneider) consist of A.C.50 cycles 3 phase 12/25 amperes trip rating push button type star delta starter complete with no volts and over load relay i/c fixing matteld board to accomondat main or sub main control switch recessed in the wall size 3’x2 ½’ i/c providing internal electric wiring for main with 3-7/0.85(7/0.36) pvc insulated wire 660 volts grade in 25 mm(1") PVC Conduct on surface as required i/c providing and fixing earthen set with 0.6mx0.6mx6.3m(2ʼx2ʼx1/4") copper plate buried in the ground and depth 3.7M(12ft or less as per pak PWD specification and testing of pumping set against required head & discharge per 72 hours etc complete(R.A Atteched) |  | P.set
2 | 32 | Manufacturing & installing MS pipe made out of MS sheet of 3/16" thick cutting and folding to requred curvature and shape i/c welding etc complete (R.A Besed on Schedule) |  | P.Rft
3 | 8 | Manufacturing & installing MS flang made out of MS sheet of 3/8" thick cutting drilling holes etc complete (R.A Besed on Schedule) |  | Each
|  |  | Total |  | 0
_________% above / below on the rates of CSR _____________/- |  |  | Amount to be added /deducted on the basis of premium quoted TOTAL
Total (A) = in words & figures :_____________________________________________________________________
____________________________________________________________________________________________
EXECUTIVE ENGINEER
| Contractor |  | BUILDINGS DIVISION
Note:- Any omissionerror if occurs will be corrected. |  |  | MATIARI

## Part-B
BILL OF QUANTITIES
Name of Work:- |  | Supplying and installing Pumping Machinery and P.L.J and testing Rising Main 6" Dia for Pir Muhallah Urban Drainage Scheme Bhitshah Taluka Hala District Matiari.
Part (B) RISING MAIN
S# | (A) Description and rate of Items based on Composite Schedule of Rates.
Item No. | Quantities | Descripition of item to be executed as site | RATE | Unit | Amount in Rupees
1 | 2500 | P/L uPVC pressure pipe of class B (equivalent make ) and fixing in trenchis i/c cutting fitting and jointing with "z" joint with one rubber ring i/c testing with water to lead of 61 meeter or 200 ft (PHSINO:1(b)P-22) | 262 | P.Rft | 655000
2 | 4219 | Dismentling cement with brick aggregate (GSINO:19(d)P-10) | 907.5 | % Cft | 38285
3 | 1406 | Dismentling C.C plain 1.2.4 (GSINO:19(c)P-10) | 3327.5 | % Cft | 46793
4 | 14063 | Excavation for pipe line in trenches and pits in soft Rock for hammering and cheisly where blosting is not pracrticable or prohibated i/c and dressing dressing side to true alignment and shapeleveling of bed of trenches to correct level and grade cutting joints holes and disposal disposal of surplus earth with in one chain as directed by engineer in charge providing fence guards light flags wherever required lift upt 5ft and lead up to one chain (PHSINO:A-6P/62 6"dia | 10770 | % 0Cft | 151453
5 | 2 | Air valve doubble acting (SOMI No.8 P-12) 3" dia | 4000 | Each | 8000
6 | 2 | Fire hydrant tee(PHSINO:7,P-16) | 1375 | Each | 2750
7 | 2 | Cost iron for special for AC pressure pipe standard wt for ACIL "B" class(PHSINO:1P-13) C.I bend 90 Degree 6" dia | 2215.5 | Each | 4425
8 | 6 | Supplying AC collars :B" Class (extra) (PHSINO:4P-5) 6" dia | 194 | Each | 1164
9 | 6 | Supplying 1 pair of rubberin Ring for AC pressure pipe "B" class and comet joints (extra) (PHSINO:7(f)P-6) | 129 | P.Pair | 774
10 | 6 | Jointing C.I/M.S flanged pipe & special inside trenchies i/c supplying rubber paking of required thickness nutts & bolts with washers etc and other tool required for jointing and testing the hoint to the specified pressure etc complete (PHSINO:1P-40) 6" dia | 887 | P.J | 5322
11 | 2 | P/chamber 2-1/2x2-1/2(750x750mm) inside dimension 4-1/2 (1372mm) deep as per approved design for S.V 3" to 12" dia cover and frame (wt kws 3qr) fixed in RCC (102mm) thick (with 5lbs steel p/cft) 9" thick (299mm) brick masonary wall set 1:6 cwt mortar (152mm) thick cwt 1:3:6 in foundation 1" (25mm thick cwt 1:2:4 flooring 1/2" (12.50mm) thick cwt i/c P/F M.S ft rest @ every one ft beyond 21/2ʼ depth curing excavation back filling and disposal of surplus earth etc complete (PHSINO:7(i)P-40) | 18820 | Each | 37640
12 | 17719 | Refilling the excavated stuff in trenches 6" thick layer i/c watering rammming to full compaction etc complete (S.I No.24 P/53) | 2760 | % Cft | 48904
|  |  | Total |  | 1000510
_________% above / below on the rates of CSR _____________/- |  |  | Amount to be added /deducted on the basis of premium quoted TOTAL
Total (A) = in words & figures :_____________________________________________________________________
____________________________________________________________________________________________
EXECUTIVE ENGINEER
| Contractor |  | BUILDINGS DIVISION
Note:- Any omissionerror if occurs will be corrected. |  |  | MATIARI