## Cover (hidden)
OFFICE OF THE
EXECUTIVE ENGINEER PHE DIVISION DADU
#REF!
#REF!
#REF!
#REF!
| Estimated cost | Rs | #REF!
PUBLIC HEALTH ENGINEERING CIRCLE LARKANA
PUBLIC HEALTH ENGINEERING DIVISION DADU

## Design (hidden)
#REF!
DESIGN OF DISPOSAL WORK AT ZONE A.
Area of Zone A. | [8 empty] | 281 | Acres
Pupolation per acre | [8 empty] | 68 | Persons
Designed population |  |  | 281 | x | 68 | = |  |  | 19108 | Persons
Daily supply | [5 empty] | = |  |  | 30 | G/H/D
Discharge |  |  | 19108 | x | 30 | x | 80% | = | 458592 | Gallons
Peek hour Discharge |  |  | 458592 | x | 3 | / | 24 | = | 57324 | Gallons
Assuming 30 mintues detention period and under working depth | [8 empty] | 6 | ft
Area of collecting tank |  |  | 57324 | x | 1 |  |  | = |  | 764.32 | ft
|  |  | 2 | x | 6 | x | 6.25
Already available facility |  |  | 1 | x | 0.785 | x | 20 | x | 20 | 314 | ft
[8 empty] | Net required |  | 450.32 | ft
No: of Collecting Tank | [7 empty] | = | 2 | Nos:
|  |  | 450.32 | / | 2 |  |  | = | 225.16 | ft
Dia of collecting tank |  |  | 225.16 | x | 4 | = | 286.828 | = | 16.93 | ft
|  |  | 3.14 |  |  |  |  | Say | 20 | ft
So provide 2 No: Additional collecting tank 20 ft, 1 No: screening chamber 10 ft dia
& Pump House 1 No: 18'x12'
DESIGN OF DELIVERY MAIN from Disposal work upto Oxidation Pond AT ZONE A
Daily Discharge | [7 empty] | = | 458592 | Gallons
Working Hours | [7 empty] | = | 8 | Hours
Discharge per hour | [7 empty] | = | 57324 | Gallons
Discharge per minute | [7 empty] | = | 955.4 | Gallons
Discharge per second | [7 empty] | = | 15.9233 | Gallons
Referring to ACIL Table
| Q | = | 16.34 | Gallons
| V | = | 3.44 | ft
| Hf | = | 0.003 | ft
| Dia | = | 12" dia
| Length | = | 8000 | Rft
Total losses |  |  | 8000 | x | 0.003 | = | 24 | Say | 24 | ft
DESIGN OF PUMPING MACHINARY AT ZONE A.
Discharge per hour | [7 empty] | = | 57324 | Gallons
Discharge per minute | [7 empty] | = | 955.4 | Gallons
No: of Pumping Set | [7 empty] | = | 2 | Sets
Discharge of each Pumping ser |  |  | 955.4 | / | 2 | = | 477.7 | Say | 850 | Gallons
Working head
| Suction lift |  |  |  | 12 | ft
| Losses of Delivery main |  |  |  | 24 | ft
| Other Losses |  |  |  | 5 | ft
| Height of Bund |  |  |  | 12 | ft
[5 empty] | 53 | ft | Say |  | 40 | ft
BHP will be | 850 | x | 40 | x | 12 | x | 100 | = | 20.6061
| 33000 |  |  | x | 60 |  |  | Say | 20 | BHP
So proposed 3 sets of Electric Motor (Siemens made) 20 BHP coupled
with KSB non clogging Pump KWPZ 100 - 250 size 5"x4" capable given
discharge 850 gallons against the head of 40 ft (1450 RPM 4 pole)
(One set as act stand bye).
Assistant Engineer
Public Health Engg: Sub-Divn:
Johi
Executive Engineer
Public Health Engg: Dvision
Dadu

## D.WORK (hidden)
PART-I RCC COLLECTING TANK
1 | Excavation of well in dry upto 20’ below ground level and disposal of | [15 empty] | 20 | + | 4 | = | 24
| soil within 1 chain in (ordinary soil) (G.S.I-1 (a) P/ 85). | [15 empty] | 10 | + | 4 | = | 14
0' to 5' depth
| C/Tank. | 2 | x | 0.785 | x | 24 | x | 24 | x | 5 |  | = | 4521.6 | Cft.
| S/Chamber. | 1 | x | 0.785 | x | 14 | x | 14 | x | 5 |  | = | 769.3 | Cft.
[13 empty] | 5290.9 | Cft.
| 5290.9 | Cft. | [9 empty] | @RS: | 2247.58 | P%0Cft | Rs: | 11891.721
2 | R.C.C work i/c all labour and material except the cost of steel reinforcement .
and its labour for b/b which will be paid separately. This rate also
i/c all kinds of formsmoulds lifting, hutting, curing, rendering and
finishing the exposed surface (i/c s/w of shingle) (a) R.C work
inroof slab beams columns rafts lintels and other structural
members laid in situ or prrecast laid in position complete in all
respect. (I) Ratio 1:2:4 Lbs cement 2 Cft, sand 4 cft shingle
1/8” to ¼” gauge. (G.S.I No. 6 P/ 16)
| Curb. | 2 | x | 3.14 | x | 21 | x | 1.5 | x | 0.5 |  | = | 98.91 | Cft.
|  | 1 | x | 3.14 | x | 11 | x | 1.5 | x | 0.5 |  | = | 25.905 | Cft.
| Trengle | 2 | x | 3.14 | x | 20.67 | x | 0.33 | + | 1.5 | 1.5 | = | 178.1609 | Cft.
2
| Trengle | 1 | x | 3.14 | x | 10.67 | x | 0.33 | + | 1.5 | 1.5 | = | 45.984 | Cft.
| Wall of | [7 empty] | 2 |  |  | A'. | 348.9599 | Cft.
| C/Tank | 2 | x | 3.14 | x | 21 | x | 1 | x | 21 |  | = | 2769.48 | Cft.
| S/C | 1 | x | 3.14 | x | 11 | x | 1 | x | 18 |  | = | 621.72 | Cft.
[12 empty] | B' | 3391.2 | Cft.
| 348.9599 |  |  | + |  | 3391.2 |  |  |  | = |  |  | 3740.1599 | Cft.
| 3740.1599 | Cft. | [9 empty] | @Rs: | 337 | P/Cft | Rs: | 1260433.8851
3 | Fabrication of mild steel reinforcement for C.C i/c cutting,
bending, laying in position making joints and fastening i/c
cost of binding wire(also i/c removal of rust from bars).(G.S.I No 8 P/ 16)
Wall.
| 3391.2 |  | x | 4.5 | / | 112 | [5 empty] | = | 136.2536 | Cwt.
Curb.
| 348.9599 |  | x | 8 | / | 112 | [5 empty] | = | 24.9257 | Cwt.
[13 empty] | 161.1793 | Cwt.
| 161.1793 | Cwt. | [9 empty] | @Rs: | 5001.7 | P/Cwt | Rs: | 806170.3964
4 | wet sinking of wells for depth below spring level by means of
drivers i/c all charges of shoring loading and removing excavated
material with in 1 chain ( in ordinary soil) ( G.S.I No 03 P/ 86 )
| 0' to 5' | 2 | x | 0.785 | x | 22.5 | x | 22.5 | x | 5 |  | = | 3974.0625 | Cft.
|  | 1 | x | 0.785 | x | 12.5 | x | 12.5 | x | 5 |  | = | 613.2812 | Cft.
[13 empty] | 4587.3438 | Cft.
| 4587.3438 | Cft. | [9 empty] | @Rs: | 11763.8 | P%0Cft | Rs: | 53964.5944
| 5' to 10' | 2 | x | 0.785 | x | 22.5 | x | 22.5 | x | 5 |  | = | 3974.0625 | Cft.
|  | 1 | x | 0.785 | x | 12.5 | x | 12.5 | x | 5 |  | = | 613.2812 | Cft.
[13 empty] | 4587.3438 | Cft.
| 4587.3438 | Cft. | [9 empty] | @Rs: | 24200 | P%0Cft | Rs: | 111013.7188
| 10' to 15' | 2 | x | 0.785 | x | 22.5 | x | 22.5 | x | 5 |  | = | 3974.0625 | Cft.
|  | 1 | x | 0.785 | x | 12.5 | x | 12.5 | x | 2 |  | = | 245.3125 | Cft.
[13 empty] | 4219.375 | Cft.
| 4219.375 | Cft. | [9 empty] | @Rs: | 37230.77 | P%0Cft | Rs: | 157090.5802
| 15' to 20' | 2 | x | 0.785 | x | 22.5 | x | 22.5 | x |  |  | = | 0 | Cft.
|  | 0 | x | 0.785 | x | 12.5 | x | 12.5 | x |  |  | = | 0 | Cft.
[13 empty] | 0 | Cft.
| 0 | Cft. | [9 empty] | @Rs: | 50416.67 | P%0Cft | Rs: | 0
| 20' to 25' | 0 | x | 0.785 | x | 22.5 | x | 22.5 | x |  |  | = | 0 | Cft.
|  | 0 | x | 0.785 | x | 12.5 | x | 12.5 | x |  |  | = | 0 | Cft.
[13 empty] | 0 | Cft.
| 0 | Cft. | [9 empty] | @Rs: | 27846.58 | P%0Cft | Rs: | 0
5 | Cement concrete Brick or stone ballest 1 ½” to 2” gauged ratio (1:4:8)
(G.S.I-4 (b) P/ 14)
|  | 2 | x | 0.785 | x | 20.67 | x | 20.67 | x | 1.5 |  | = | 1006.1712 | Cft.
|  | 1 | x | 0.785 | x | 10.67 | x | 10.67 | x | 1.5 |  | = | 134.0571 | Cft.
|  | 2 | x | 0.785 | x | 19.5 | x | 19.5 | x | 0.5 |  | = | 298.4963 | Cft.
|  | 1 | x | 0.785 | x | 9.5 | x | 9.5 | x | 0.5 |  | = | 35.4231 | Cft.
[13 empty] | 1474.1476 | Cft.
| 1474.1476 | Cft. | [9 empty] | @Rs: | 9416.28 | P% Cft | Rs: | 138809.867
6 | Cement concrete plain i/c placing compacting finishing and curing
complete i/c screening and washing of stone aggregate without shuttering
(GSI No. 5 p/ 15)
i) | (Ratio 1:4:8)
|  | 2 | x | 0.785 | x | 20 | x | 20 | x | 1.5 |  | = | 942 | Cft.
|  | 1 | x | 0.785 | x | 10 | x | 10 | x | 1 |  | = | 78.5 | Cft.
[13 empty] | 1020.5 | Cft.
| 1020.5 | Cft. | [9 empty] | @Rs: | 11288.75 | P% Cft | Rs: | 115201.6938
ii) | (Ratio 1:3:6)
|  | 2 | x | 0.785 | x | 20 | x | 20 | x | 1.5 |  | = | 942 | Cft.
|  | 1 | x | 0.785 | x | 10 | x | 10 | x | 1 |  | = | 78.5 | Cft.
[13 empty] | 1020.5 | Cft.
| 1020.5 | Cft. | [9 empty] | @Rs: | 12595 | P% Cft | Rs: | 128531.975
iii) | (Ratio 1:2:4)
|  | 2 | x | 0.785 | x | 20 | x | 20 | x | 1.5 |  | = | 942 | Cft.
|  | 1 | x | 0.785 | x | 10 | x | 10 | x | 1 |  | = | 78.5 | Cft.
[13 empty] | 1020.5 | Cft.
| 1020.5 | Cft. | [9 empty] | @Rs: | 14429.25 | P% Cft | Rs: | 147250.4962
7 | Bailing or pumping out sub soil water during excavated concerting cost in situ
concrete or masonary work information etc complete (P.H.S-I/ 18 P/ 75)
| 1st Opration | 2 | x | 0.785 | x | 20 | x | 20 | x | 16 |  | = | 10048 | Cft.
|  | 1 | x | 0.785 | x | 10 | x | 10 | x | 9 |  | = | 706.5 | Cft.
| 2nd opration | 2 | x | 0.785 | x | 20 | x | 20 | x | 12 |  | = | 7536 | Cft.
|  | 1 | x | 0.785 | x | 10 | x | 10 | x | 6 |  | = | 471 | Cft.
[13 empty] | 18761.5 | Cft.
| 18761.5 | Cft. | [9 empty] | @Rs: | 543 | P%Cft | Rs: | 101874.945
8 | Providing Construction joints in concrete work of 9” (225mm)
made corrugated P.V.C water stop (with bulb) i/c soldering, cost
of material and labour ( P.H.S.I -1 P/ 56)
|  | 2 | x | 3 | x | 3.14 | x | 21 |  |  |  | = | 395.64 | Rft.
|  | 1 | x | 2 | x | 3.14 | x | 11 |  |  |  | = | 69.08 | Rft.
[13 empty] | 464.72 | Rft.
| 464.72 | Rft. | [9 empty] | @Rs: | 86 | P/Rft | Rs: | 39965.92
9 | Fabrication of heavy steel work with angles tees flats, iron, round and sheet
iron for making trusses, girding tank etc. including cutting riveting handling
erection in position ( G.S.I -2 P/ 90).
| S/Jalli | 1 | x | 3.5 | [7 empty] | = | 3.5 | Cwt
[13 empty] | 3.5 | Cwt
| 3.5 | Cwt | [9 empty] | @Rs: | 4928.49 | P/Cwt | Rs: | 17249.715
10 | Erection and fitting in position of iron trusses staging of water tank etc
( G.S.I-3 P/ 90)
| 3.5 | Cwt | [9 empty] | @Rs: | 271.04 | P/Cwt | Rs: | 948.64
11 | Excavation for pipe lines in trenches in pits in soft soil i/c
trimming dressing sides to true alignment shape leveling
of beds of trenches to correct level and grade cutting joints holes and
disposal of surplus earth within one chain as direct by
engineer incharge providing fence guards lights whenever
and temporary crossing for non vehicular traffic whenever required
lift upto 5 Ft and lead upto one chain (P.H.S.I. No. 1 P/ 60)
| 0' to 5' Depth | 2 | x | 16 | x | 5 | x | 5 |  |  |  | = | 800 | Cft.
| 800 | Cft. | [9 empty] | @Rs: | 3600 | P%0 Cft | Rs: | 2880
12 | Excavation for pipe lines in trenches in pits in wet soil i/c
trimming dressing sides to true alignment shape leveling
of beds of trenches to correct level and grade cutting joints holes and
disposal of surplus earth within one chain as direct by
engineer incharge providing fence guards lights whenever
and temporary crossing for non vehicular traffic whenever required
lift upto 5 Ft and lead upto one chain (P.H.S.I. No. 14 P/ 66)
| 5' to 8' Depth | 2 | x | 16 | x | 5 | x | 3 |  |  |  | = | 480 | Cft.
| 480 | Cft. | [9 empty] | @Rs: | 5950 | P%0 Cft | Rs: | 2856
| 8' to 11' Depth | 2 | x | 16 | x | 5 | x | 3 |  |  |  | = | 480 | Cft.
| 480 | Cft. | [9 empty] | @Rs: | 6500 | P%0 Cft | Rs: | 3120
13 | Excavation for pipe lines in trenches in pits in Slush or Daldal Soil i/c
trimming dressing sides to true alignment shape leveling
of beds of trenches to correct level and grade cutting joints holes and
disposal of surplus earth within one chain as direct by
engineer incharge providing fence guards lights whenever
and temporary crossing for non vehicular traffic whenever required
lift upto 5 Ft and lead upto one chain (P.H.S.I. No. 15 P/ 67)
| 11'to14' Depth | 2 | x | 16 | x | 5 | x | 1 |  |  |  | = | 160 | Cft.
| 160 | Cft. | [9 empty] | @Rs: | 12450 | P%0Cft | Rs: | 1992
14 | Providing and R.C.C Pipe of A.S.T.M C-76-62 T/C-76-70 Class-II wall-B and
fixing in trenches i/c cutting fitting and jointing with rubber ring i/c testing
with water to specified pressure (P/H.S-I -1 P/17)
| 18" dia | 2 | x | 16 | [7 empty] | = | 32 | Rft
| 32 | Rft | [9 empty] | @Rs: | 618 | P/Rft | Rs: | 19776
15 | Refilling the Excavated stuff in trenches 6” thick layers leveling
i/c watering ramming to full compaction etc complete
(P.H.S.I. No.24 P/ 77)
| Qtty: of Item No. |  | 11 | + |  | 12 | + | 13 |  |  |  | = | 1920 | Cft.
| 1920 |  | x | 0.9 | [7 empty] | = | 1728 | Cft.
| 1728 | Cft. | [9 empty] | @Rs: | 2760 | P%0Cft | Rs: | 4769.28
16 | Pacca brick work in foundation and plinth in cement sand mortar(1:6)
(G.S.I No. 4 P/ 20)
|  | 1 | x | 10 | x | 1.13 | x | 2 |  |  |  | = | 22.6 | Cft
|  | 2 | x | 1.13 | x | 1.13 | x | 6 |  |  |  | = | 15.3228 | Cft
[13 empty] | 37.9228 | Cft
| 37.9228 | Cft | [9 empty] | @rs: | 11948.36 | P%Cft | Rs: | 4531.1527
17 | Cement, Plaster (1:4) up to 12’ height ½” thick (G.S.I. No.11 P/51)
|  | 1 | x | 10 | x | 2.25 | [5 empty] | = | 22.5 | Sft.
|  | 2 | x | 3 | x | 1.13 | x | 8 |  |  |  | = | 54.24 | Sft.
[13 empty] | 76.74 | Sft.
| 76.74 | Sft. | [9 empty] | @Rs: | 2283.93 | P%Sft | Rs: | 1752.6879
[14 empty] | Total | Rs: | 3132075.2684
18 | Cartage of Material
#REF!
| 3774.06 | Cft | [9 empty] | @Rs: | #REF! | P%Cft | Rs: | #REF!
#REF!
| 6107.9207 | Cft | [9 empty] | @Rs: | #REF! | P%Cft | Rs: | #REF!
#REF!
| 1415.1817 | Cft | [9 empty] | @Rs: | #REF! | P%Cft | Rs: | #REF!
#REF!
| 511.9578 | Nos: | [9 empty] | @Rs: | #REF! | P%0Nos: | Rs: | #REF!
#REF!
| 1205.6079 | Bags | [9 empty] | @Rs: | #REF! | P/Bag | Rs: | #REF!
Carriage of Earth (Lead 3.0 Mile)
|  | Cft | [9 empty] | @Rs: | 579.41 | P%Cft | Rs: | 0
Carriage of Pipe from Hyderabad
| (Lead | #REF! |  | Miles)
| 32 | Rft |  | 18" dia | [7 empty] | @Rs: | #REF! | P%Rft | Rs: | #REF!
[15 empty] | Rs: | #REF!
[13 empty] | Schedule Items |  | Rs | 3132075.2684
[13 empty] | Non Sch: Items |  | Rs | 0
[15 empty] | Rs | #REF!
[9 empty] | Ded: |  | 0% |  | below |  | Rs | #REF!
[14 empty] | Net | Rs | #REF!
Assistant Engineer
Public Health Engg: Sub-Divn:I
Larkano
Executive Engineer
Public Health Engg: Dvision-I
Larkano

## M.stat (hidden)
Material Statement
Collecting Tank
S.No: | Item | Qty: | Bajri | Stone | Hill sand | Cement | Brock
| C.C Stone Ballest 1:4:8 | 1474.1476 | 0 | 1415.1817 | 707.5909 | 141.5182 | 0
3 | Pacca Brick Work 1:6 | 37.9228 | 0 | 0 | 9.7462 | 1.3045 | 511.9578
| R.C.C Well Crub |  | 0 | 0 | 0 | 0 | 0
| Cement Plaster 1:4 1/2" Thick | 76.74 | 0 | 0 | 2.7626 | 0.39905 | 0
| C.C Plain 1:4:8 | 1020.5 | 979.68 | 0 | 489.84 | 97.968 | 0
| C.C. Plain 1:3:6 | 1020.5 | 938.86 | 0 | 469.43 | 132.665 | 0
| C.C Plain 1:2:4 | 1020.5 | 898.04 | 0 | 449.02 | 173.485 | 0
| R.C.C 1:2:4 | 3740.1599 | 3291.3407 | 0 | 1645.6704 | 658.2681 | 0
| Total |  | 6107.9207 | 1415.1817 | 3774.06 | 1205.6079 | 511.9578
Assistant Engineer
Public Health Engg: Sub-Division-I
Larkano

## S.Quarter (hidden)
#REF!
1 | Excavation in foundation of building bridges and other structures.
I/c dag belling dressing refilling around the structures with excavated
Earth watering ramming lead up to one chain and lift up to 5’ (G.S.I. No. 18 P/ 04)
| Long Wall | 1 | x | 12.62 | x | 2 | x | 1.75 | = | 44.17 | Cft.
|  | 2 | x | 14.75 | x | 2 | x | 1.75 | = | 103.25 | Cft.
|  | 1 | x | 21.5 | x | 2 | x | 1.75 | = | 75.25 | Cft.
|  | 1 | x | 21.87 | x | 1.5 |  |  | = | 32.805 | Cft.
|  | 1 | x | 21.5 | x | 2 | x | 1.75 | = | 75.25 | Cft.
| Short wall | 2 | x | 8.93 | x | 2 | x | 1.75 | = | 62.51 | Cft.
|  | 2 | x | 9.13 | x | 2 | x | 1.75 | = | 63.91 | Cft.
|  | 4 | x | 2.75 | x | 2 | x | 1.75 | = | 38.5 | Cft.
|  | 1 | x | 15.5 | x | 1.5 | x | 1 | = | 23.25 | Cft.
|  | 1 | x | 4.5 | x | 2.21 | x | 0.5 | = | 4.9725 | Cft.
| Steps | 1 | x | 4.5 | x | 1.25 | x | 0.5 | = | 2.8125 | Cft.
[10 empty] | 526.68 | Cft.
| 526.68 | Cft. | [7 empty] | @Rs: | 3176.25 | P%0 Cft | Rs: | 1672.8673
2 | Cement concrete brick or stone ballast 1 ½” to 2” gauge.
(Ratio 1:4:8) (G.S.I No. 4 P/ 14)
| Long Wall | 1 | x | 12.62 | x | 2 | x | 0.75 | = | 18.93 | Cft.
|  | 2 | x | 14.75 | x | 2 | x | 0.75 | = | 44.25 | Cft.
|  | 1 | x | 21.5 | x | 2 | x | 0.75 | = | 32.25 | Cft.
|  | 1 | x | 21.5 | x | 2 |  | 0.75 | = | 32.25 | Cft.
|  | 1 | x | 21.5 | x | 2 | x | 0.75 | = | 32.25 | Cft.
|  | 1 | x | 21.37 | x | 1.5 | x | 0.5 | = | 16.0275 | Cft.
| Short wall | 2 | x | 8.93 | x | 2 | x | 0.75 | = | 26.79 | Cft.
|  | 2 | x | 9.13 | x | 2 | x | 0.75 | = | 27.39 | Cft.
|  | 4 | x | 2.75 | x | 2 | x | 0.75 | = | 16.5 | Cft.
|  | 1 | x | 15.75 | x | 1.5 | x | 0.5 | = | 11.8125 | Cft.
|  | 1 | x | 4.5 | x | 2.25 | x | 0.5 | = | 5.0625 | Cft.
| Steps | 1 | x | 4.5 | x | 1.25 | x | 0.5 | = | 2.8125 | Cft.
[10 empty] | 266.325 | Cft.
| 266.325 | Cft | [7 empty] | @Rs: | 9416.28 | P%Cft | Rs: | 25077.9077
3 | Cement concrete plain i/c placing compacting finishing and
curing complete i/c screening and washing of stone aggregate
without shuttering (Ratio 1:3:6) (G.S.I.No 5 P/ 15)
| Long Wall | 1 | x | 12.21 | x | 1 | x | 2.5 | = | 30.525 | Cft.
|  | 2 | x | 13.87 | x | 1 | x | 2.5 | = | 69.35 | Cft.
|  | 1 | x | 21.5 | x | 1 | x | 2.5 | = | 53.75 | Cft.
|  | 1 | x | 21.72 | x | 1 |  | 1.5 | = | 32.58 | Cft.
|  | 1 | x | 21.5 | x | 1 | x | 2.5 | = | 53.75 | Cft.
| Short wall | 2 | x | 9.62 | x | 1 | x | 2.5 | = | 48.1 | Cft.
|  | 2 | x | 9.37 | x | 1 | x | 2.5 | = | 46.85 | Cft.
|  | 1 | x | 16.37 | x | 1 | x | 1.5 | = | 24.555 | Cft.
|  | 1 | x | 16.37 | x | 1 | x | 1.5 | = | 24.555 | Cft.
|  | 1 | x | 4 | x | 3 | x | 0.5 | = | 6 | Cft.
|  | 1 | x | 4 | x | 2 | x | 0.5 | = | 4 | Cft.
|  | 1 | x | 4 | x | 1 | x | 0.5 | = | 2 | Cft.
[10 empty] | 396.015 | Cft.
| 396.015 | Cft | [7 empty] | @Rs: | 12595 | P%Cft | Rs: | 49878.0892 | 26701
4 | Erection and removal of centering for R.C.C or plain C.C Work
of Partal Wood 1st class(vertical). (G.S.I.No. 19 P/ 17)
| Long Wall | 1 | x | 2 | x | 12.21 | x | 2.5 | = | 61.05 | Sft
|  | 2 | x | 2 | x | 13.87 | x | 2.5 | = | 138.7 | Sft
|  | 1 | x | 2 | x | 21.5 | x | 2.5 | = | 107.5 | Sft
|  | 1 | x | 2 | x | 21.72 |  | 1.5 | = | 65.16 | Sft
|  | 1 | x | 2 | x | 21.5 | x | 2.5 | = | 107.5 | Sft
| Short wall | 2 | x | 2 | x | 9.62 | x | 2.5 | = | 96.2 | Sft
|  | 2 | x | 2 | x | 9.37 | x | 2.5 | = | 93.7 | Sft
|  | 1 | x | 2 | x | 16.37 | x | 1.5 | = | 49.11 | Sft
|  | 1 | x | 2 | x | 16.37 | x | 1.5 | = | 49.11 | Sft
|  | 1 | x | 2 | x | 4 | x | 0.5 | = | 4 | Sft
|  | 1 | x | 2 | x | 4 | x | 0.5 | = | 4 | Sft
[10 empty] | 776.03 | Sft
| 776.03 | Sft | [7 empty] | @Rs: | 3127.41 | P%Sft | Rs | 24269.6398 | 13229
5 | Filling Watering and ramming earth in floor with new earth excavated from
out side lead upto 1 chain and lift upto 5' (G.S.I No 22 P- 4)
|  | 1 | x | 9.62 | x | 6.62 | x | 1 | = | 63.6844 | Cft.
|  | 1 | x | 9.62 | x | 11.62 | x | 1 | = | 111.7844 | Cft.
|  | 1 | x | 4.62 | x | 6.62 | x | 1 | = | 30.5844 | Cft.
|  | 1 | x | 3.62 | x | 3.45 |  | 1 | = | 12.489 | Cft.
|  | 1 | x | 3.62 | x | 2.93 | x | 1 | = | 10.6066 | Cft.
|  | 1 | x | 20.38 | x | 16.38 | x | 0.62 | = | 206.9711 | Cft.
|  | 1 | x | 9.62 | x | 3.31 | x | 0.62 | = | 19.7422 | Cft.
|  | 1 | x | 4 | x | 4 | x | 0.62 | = | 9.92 | Cft.
[10 empty] | 465.7821 | Cft.
| 465.7821 | Cft | [7 empty] | @Rs: | 3630 | P%0Cft | Rs: | 1690.789 | 1249
6 | Pacca brick work in ground floor cement, sand, mortar (1:6)
(G.S.I. No 5 P/ 20)
| Long Wall | 1 | x | 12 | x | 0.75 | x | 9.62 | = | 86.58 | Cft.
|  | 2 | x | 13.5 | x | 0.75 | x | 11.62 | = | 235.305 | Cft.
|  | 1 | x | 7.75 | x | 0.75 | x | 9.62 | = | 55.9162 | Cft.
|  | 1 | x | 9.38 | x | 0.75 |  | 9.62 | = | 67.6767 | Cft.
|  | 1 | x | 4.35 | x | 0.75 | x | 7.5 | = | 24.4687 | Cft.
|  | 3 | x | 0.75 | x | 0.75 | x | 7.5 | = | 12.6562 | Cft.
|  | 3 | x | 6.16 | x | 0.37 | x | 7.5 | = | 51.282 | Cft.
|  | 1 | x | 7.75 | x | 0.75 |  | 9.62 | = | 55.9162 | Cft.
|  | 1 | x | 9.38 | x | 0.75 | x | 9.62 | = | 67.6767 | Cft.
| Short wall | 2 | x | 10 | x | 0.75 | x | 9.62 | = | 144.3 | Cft.
|  | 2 | x | 10 | x | 0.75 | x | 11.62 | = | 174.3 | Cft.
|  | 3 | x | 4 | x | 0.75 | x | 9.62 | = | 86.58 | Cft.
|  | 1 | x | 4 | x | 0.37 | x | 9.62 | = | 14.2376 | Cft.
|  | 1 | x | 7.5 | x | 0.75 | x | 7.13 | = | 40.1063 | Cft.
|  | 1 | x | 9.25 | x | 0.37 | x | 7.13 | = | 24.4024 | Cft.
[10 empty] | 1141.4042 | Cft.
Deduction
|  | 2 | x | 4.5 | x | 0.75 |  |  | = | 6.75 | Cft
|  | 2 | x | 5.5 | x | 0.75 | x | 0.58 | = | 4.785 | Cft
|  | 2 | x | 3 | x | 0.75 | x | 7 | = | 31.5 | Cft
|  | 2 | x | 4.75 | x | 0.58 |  |  | = | 5.51 | Cft
|  | 1 | x | 3 | x | 0.75 | x | 7 | = | 15.75 | Cft
|  | 2 | x | 3 | x | 0.75 | x | 7 | = | 31.5 | Cft
|  | 1 | x | 2.91 | x | 0.75 | x | 4 | = | 8.73 | Cft
|  | 1 | x | 2.25 | x | 0.75 | x | 4 | = | 6.75 | Cft
|  | 1 | x | 3 | x | 0.38 | x | 4 | = | 4.56 | Cft
|  | 1 | x | 10 | x | 0.75 | x | 0.58 | = | 4.35 | Cft
|  | 1 | x | 3.4 | x | 0.75 | x | 0.58 | = | 1.479 | Cft
|  | 1 | x | 2.5 | x | 0.75 | x | 7 | = | 13.125 | Cft
|  | 1 | x | 8 | x | 0.75 | x | 0.75 | = | 4.5 | Cft
|  | 1 | x | 1 | x | 0.75 | x | 1.25 | = | 0.9375 | Cft
|  | 1 | x | 5.5 | x | 0.75 | x | 0.58 | = | 2.3925 | Cft
|  | 2 | x | 2.5 | x | 0.75 | x | 7 | = | 26.25 | Cft
|  | 1 | x | 2.5 | x | 0.75 | x | 0.58 | = | 1.0875 | Cft
|  | 2 | x | 1.5 | x | 0.75 | x | 1.75 | = | 3.9375 | Cft
|  | 2 | x | 3.5 | x | 0.75 | x | 0.58 | = | 3.045 | Cft
|  | 2 | x | 2.5 | x | 0.75 | x | 0.58 | = | 2.175 | Cft
|  | 3 | x | 5 | x | 0.75 | x | 0.72 | = | 8.1 | Cft
|  | 1 | x | 4 | x | 0.75 | x | 0.58 | = | 1.74 | Cft
[10 empty] | 188.954 | Cft
| Net Qutty: | 1141.4042 |  |  | - | 188.954 |  |  | = | 952.4502 | Cft
| 952.4502 | Cft | [7 empty] | @Rs: | 12674.36 | P%Cft | Rs: | 120716.964 | 40424
7 | R.C.C work i/c all labour and material except the cost of steel
reinforcement and its labour for b/b which will be paid separately.
This rate also i/c all kinds of forms moulds lifting, shutting, curing,
rendering and finishing the exposed surface (i/c s/w of shingle) (a) R.C work in
roof slab beams columns rafts lintels and other structural members laid in
situ or prrecast laid in position complete in all respect. (I) Ratio 2:2:4 Lbs
cement2 Cft, sand 4 cft shingle1/8” to ¼” gauge. (G.S.I No. 6 P/ 16).
|  | 1 | x | 13.38 | x | 16 | x | 0.38 | = | 81.3504 | Cft.
|  | 1 | x | 7.5 | x | 9 | x | 0.38 | = | 25.65 | Cft.
|  | 1 | x | 3.75 | x | 1.5 | x | 0.38 | = | 2.1375 | Cft.
|  | 1 | x | 15.25 | x | 16.5 |  | 0.38 | = | 95.6175 | Cft.
|  | 1 | x | 10 | x | 0.75 | x | 0.38 | = | 2.85 | Cft.
|  | 2 | x | 5 | x | 0.75 | x | 0.58 | = | 4.35 | Cft.
|  | 2 | x | 4 | x | 0.75 | x | 0.58 | = | 3.48 | Cft.
|  | 1 | x | 10 | x | 0.75 |  | 0.58 | = | 4.35 | Cft.
|  | 1 | x | 3.5 | x | 0.75 | x | 0.58 | = | 1.5225 | Cft.
|  | 1 | x | 4 | x | 0.75 | x | 0.58 | = | 1.74 | Cft.
|  | 1 | x | 5.5 | x | 0.75 | x | 0.58 | = | 2.3925 | Cft.
|  | 2 | x | 2.5 | x | 0.75 | x | 0.58 | = | 2.175 | Cft.
|  | 2 | x | 3.5 | x | 0.75 | x | 0.58 | = | 3.045 | Cft.
|  | 2 | x | 2.5 | x | 0.75 | x | 0.58 | = | 2.175 | Cft.
|  | 1 | x | 4 | x | 0.75 | x | 0.58 | = | 1.74 | Cft.
|  | 1 | x | 61.5 | x | 0.25 | x | 1.25 | = | 19.2188 | Cft.
|  | 1 | x | 37.75 | x | 0.25 | x | 1.25 | = | 11.7969 | Cft.
|  | 1 | x | 3.5 | x | 0.25 | x | 2 | = | 1.75 | Cft.
|  | 1 | x | 2 | x | 0.25 | x | 2 | = | 1 | Cft.
|  | 1 | x | 3.5 | x | 0.25 | x | 0.3 | = | 0.2625 | Cft.
|  | 1 | x | 5.5 | x | 0.87 | x | 0.25 | = | 1.1963 | Cft.
[10 empty] | 269.7998 | Cft.
| 269.7998 | Cft | [7 empty] | @Rs: | 337 | P/Cft | Rs: | 90922.5242 | 36059
8 | Fabrication of mild steel reinforcement for C.C i/c cutting, bending,
laying in position making joints and fastening i/c cost of binding wire
(also i/c removal of rust from bars).(G.S.I No 8 P/ 16)
| 269.7998 | x |  | 4.5 | / | 112 |  |  | = | 10.8402 | Cwt
| 10.8402 | Cwt | [7 empty] | @Rs: | 5001.7 | P/Cwt | Rs: | 54219.2759 | 21457
8 | First class deodar wood wrought joinery in doors and windows
etc: fixed in position i/c chowkate hold joints ings iron tower bolts
chocks cleats handles and cords with hooks etc: deodar panneled or
pannelled and glazed or full glazed 1-3/4" thick. (G.S.I-7, P-58).
|  |  |  | 2 | x | 3 | x | 7 | = | 42 | Sft
|  |  |  | 1 | x | 3 | x | 7 | = | 21 | Sft
|  |  |  | 1 | x | 2.5 | x | 7 | = | 17.5 | Sft
|  |  |  | 1 | x | 2.91 |  | 4 | = | 11.64 | Sft
|  |  |  | 1 | x | 2.25 | x | 4 | = | 9 | Sft
|  |  |  | 1 | x | 2.5 | x | 4 | = | 10 | Sft
|  |  |  | 1 | x | 1.58 | x | 4 | = | 6.32 | Sft
|  |  |  | 1 | x | 1 | x | 1.25 | = | 1.25 | Sft
|  |  |  | 2 | x | 2.5 | x | 7 | = | 35 | Sft
|  |  |  | 1 | x | 3.5 | x | 1.75 | = | 6.125 | Sft
|  |  |  | 1 | x | 5 | x | 7 | = | 35 | Sft
[10 empty] | 194.835 | Sft
| 194.835 | Sft | [7 empty] | @Rs: | 1273.76 | P/Sft | Rs | 248173.0296 | 13229
8 | Providing and fixing deodar almarah 9"x12" depth i/c boring
with lock shalves shutters bress fitting complete. (GSI-23 P-60)
|  |  |  | 1 | x | 3 | x | 4 | = | 12 | Sft
| 12 | Sft | [7 empty] | @Rs: | 1778.5 | P/Sft | Rs | 21342 | 13229
8 | Providing and fixing ornamental cement Jali 2" thick (1:2:4) without steel
(GSI-11 P-17)
| Verandah |  |  | 2 | x | 4.5 | x | 4 | = | 36 | Sft
| 36 | Sft | [7 empty] | @Rs: | 226.02 | P/Sft | Rs | 8136.72 | 13229
8 | Galianized wire gauge fixed to chowkates with 3/4" deodar strips and serews.
(GSI-14 (d), P-59)
|  |  |  | 1 | x | 2.5 | x | 4 | = | 10 | Sft
|  |  |  | 1 | x | 2.25 | x | 4 | = | 9 | Sft
|  |  |  | 1 | x | 1.58 | x | 4 | = | 6.32 | Sft
[10 empty] | 25.32 | Sft
| 25.32 | Sft | [7 empty] | @Rs: | 190.72 | P/Sft | Rs | 4829.0304 | 13229
2 | Cement concrete brick or stone ballast 1 ½” to 2” gauge.
(Ratio 1:4:8) (G.S.I No. 4 P/ 14)
|  | 1 | x | 14.62 | x | 6.62 | x | 0.25 | = | 24.1961 | Cft.
|  | 1 | x | 9.62 | x | 11.62 | x | 0.25 | = | 27.9461 | Cft.
|  | 1 | x | 3.62 | x | 3.43 | x | 0.25 | = | 3.1042 | Cft.
|  | 1 | x | 3.62 | x | 3.43 |  | 0.25 | = | 3.1042 | Cft.
|  | 1 | x | 3.62 | x | 3.43 | x | 0.25 | = | 3.1042 | Cft.
[10 empty] | 61.4546 | Cft.
| 61.4546 | Cft | [7 empty] | @Rs: | 9416.28 | P%Cft | Rs: | 5786.7419
9 | Providing and laying 1” thick to toping Cement Concrete (1:2:4) I/c surface,
finishing and dividing in to panels (GSI No. 16 P/41)
| 3" thick |  |  | 1 | x | 10 | x | 7 | = | 70 | Sft
|  |  |  | 1 | x | 10 | x | 12 | = | 120 | Sft
|  |  |  | 1 | x | 4 | x | 7 | = | 28 | Sft
|  |  |  | 1 | x | 4 | x | 4 | = | 16 | Sft
|  |  |  | 1 | x | 4 | x | 3.5 | = | 14 | Sft
[10 empty] | 248 | Sft
| 248 | Sft |  | 3" thick | [5 empty] | @Rs: | 4411.82 | P%Sft | Rs: | 10941.3136 | 5294
9 | Dry brick on edge paving sand grouted i/c preparation of bed by
watering ramming and bringing the same to proper camber by
1/2" thick mud plaster. (G.S.I-5, P-39).
|  |  |  | 1 | x | 20.28 | x | 16.38 | = | 332.1864 | Sft
|  |  |  | 1 | x | 9.62 | x | 3.31 | = | 31.8422 | Sft
|  |  |  | 1 | x | 4 | x | 4 | = | 16 | Sft
[10 empty] | 380.0286 | Sft
| 380.0286 | Sft | [7 empty] | @Rs: | 3823.57 | P%Sft | Rs: | 14530.6595 | 5294
9 | Cutting and fixing iron bars for barred windows. (G.S.I-18, P-91).
|  |  |  | 1 | x | 3 | x | 5 | = | 15 | Bars
| 15 | Bars | [7 empty] | @Rs: | 28.23 | P/Bar | Rs: | 423.45 | 5294
10 | Cement, Plaster (1:6) up to 12’ height ½” thick (G.S.I. No.13 P/51)
|  | 2 | x( | 10 | + | 7 | )x | 9.62 |  |  | = | 327.08 | Sft
|  | 2 | x( | 10 | + | 12 | )x | 11.62 |  |  | = | 511.28 | Sft
|  | 2 | x( | 4 | + | 7 | )x | 9.62 |  |  | = | 211.64 | Sft
|  | 2 | x( | 4 | + | 4 | )x | 9.62 |  |  | = | 153.92 | Sft
|  | 1 | x( | 4 | + | 3 | + | 5 | )x | 9.62 | = | 115.44 | Sft
|  | 1 | x | 10 | x | 9.62 |  |  |  |  | = | 96.2 | Sft
|  | 1 | x | 4 | x | 11.62 |  |  |  |  | = | 46.48 | Sft
|  | 1 | x | 7 | x | 11.62 |  |  |  |  | = | 81.34 | Sft
|  | 1 | x | 7.75 | x | 9.62 |  |  |  |  | = | 74.555 | Sft
|  | 1 | x | 4.75 | x | 9.62 |  |  |  |  | = | 45.695 | Sft
|  | 1 | x | 4.75 | x | 9.62 |  |  |  |  | = | 45.695 | Sft
|  | 1 | x | 4.75 | x | 9.62 |  |  |  |  | = | 45.695 | Sft
|  | 1 | x | 8.62 | x | 9.62 |  |  |  |  | = | 82.9244 | Sft
|  | 1 | x | 7.5 | x | 7 |  |  |  |  | = | 52.5 | Sft
|  | 1 | x | 24 | x | 6.75 |  |  |  |  | = | 162 | Sft
|  | 3 | x | 5.41 | x | 6.75 |  |  |  |  | = | 109.5525 | Sft
|  | 1 | x | 3.5 | x | 9.62 |  |  |  |  | = | 33.67 | Sft
|  | 1 | x | 1.85 | x | 7 |  |  |  |  | = | 12.95 | Sft
|  | 2 | x | 1.13 | x | 7 |  |  |  |  | = | 15.82 | Sft
|  | 1 | x | 11.13 | x | 11.62 |  |  |  |  | = | 129.3306 | Sft
|  | 1 | x | 1.5 | x | 11.63 |  |  |  |  | = | 17.445 | Sft
|  | 1 | x | 10.75 | x | 9.63 |  |  |  |  | = | 103.5225 | Sft
|  | 1 | x | 12 | x | 9.62 |  |  |  |  | = | 115.44 | Sft
|  | 1 | x | 21.5 | x | 6.75 |  |  |  |  | = | 145.125 | Sft
|  | 6 | x | 0.25 | x | 6.75 |  |  |  |  | = | 10.125 | Sft
|  | 1 | x | 0.75 | x | 7 |  |  |  |  | = | 5.25 | Sft
|  | 1 | x | 9.25 | x | 6.75 |  |  |  |  | = | 62.4375 | Sft
|  | 1 | x | 7.5 | x | 7 |  |  |  |  | = | 52.5 | Sft
|  | 1 | x | 5.5 | x | 9.62 |  |  |  |  | = | 52.91 | Sft
|  | 1 | x | 9.58 | x | 9.62 |  |  |  |  | = | 92.1596 | Sft
|  | 1 | x | 4.28 | x | 7 |  |  |  |  | = | 29.96 | Sft
|  | 1 | x | 7.75 | x | 9.62 |  |  |  |  | = | 74.555 | Sft
|  | 1 | x | 13.5 | x | 11.62 |  |  |  |  | = | 156.87 | Sft
|  | 1 | x | 4 | x | 1 |  |  |  |  | = | 4 | Sft
|  | 1 | x | 2 | x | 0.5 |  |  |  |  | = | 1 | Sft
|  | 1 | x | 4 | x | 0.5 |  |  |  |  | = | 2 | Sft
|  | 2 | x | 4 | x | 0.5 |  |  |  |  | = | 4 | Sft
|  | 2 | x | 4 | x | 0.5 |  |  |  |  | = | 4 | Sft
|  | 2 | x | 1 | x | 0.5 |  |  |  |  | = | 1 | Sft
|  | 2 | x | 2 | x | 0.5 |  |  |  |  | = | 2 | Sft
|  | 1 | x | 11.34 | x | 1.5 |  |  |  |  | = | 17.01 | Sft
|  | 1 | x | 1.5 | x | 1.5 |  |  |  |  | = | 2.25 | Sft
|  | 1 | x | 10.96 | x | 1.5 |  |  |  |  | = | 16.44 | Sft
|  | 1 | x | 12.21 | x | 1.5 |  |  |  |  | = | 18.315 | Sft
|  | 1 | x | 21.17 | x | 1.5 |  |  |  |  | = | 31.755 | Sft
|  | 1 | x | 17.71 | x | 1 |  |  |  |  | = | 17.71 | Sft
|  | 1 | x | 5.71 | x | 1.5 |  |  |  |  | = | 8.565 | Sft
|  | 1 | x | 9.75 | x | 1.5 |  |  |  |  | = | 14.625 | Sft
|  | 1 | x | 4.38 | x | 1 |  |  |  |  | = | 4.38 | Sft
|  | 1 | x | 21.56 | x | 1.5 |  |  |  |  | = | 32.34 | Sft
[11 empty] | 3453.4571 |  | Sft
Deduction
| Qty: same as item No: |  |  |  |  | 8 |  |  |  |  | = | 194.835 | Sft
[10 empty] | Net | 3258.6221 |  | Sft
| 3258.6221 | Sft | [7 empty] | @Rs: | 2206.6 | P%Sft | Rs: | 71904.7553 | 8297
11 | Cement, Plaster (1:4) up to 12’ height 3/8” thick (G.S.I. No.11 P/51)
| 0 | Sft | [7 empty] | @Rs: | 2197.52 | P%Sft | Rs: | 0 | 8263
12 | Cement, Pointing struck joint on walls (1:3) (G.S.I. No.19 P/52)
| 0 | Sft | [7 empty] | @Rs: | 1213.58 | P%Sft | Rs: | 0 | 5291
13 | Making and fixing steel grated door with 1/16” thick sheeting i/c angle iron
frame 2”x2”x 3/8” and ¾” sq: bars 4” Center to center with
locking arrangement (G.S.I. No.24 P/91)
| Door | 0 | x | 0 | x | 8 |  |  | = | 0 | Sft
| 0 | Sft | [7 empty] | @Rs: | 726.72 | P/Sft | Rs: | 0 | 20348
14 | Fabrication of heavy steel work with angles tees, flat iron round iron and sheet iron
for making trsses girders, tanks etc: i/c cutting tanks etc: i/c cutting drilling riveting
handling assembling and fixing but excluding erection in positiion. (G.S.I- 2, P-90)
| Window | 3 |  | 3 | x | 4 | x | 9.5 | / | 112 | = | 3.0536 | Cwt
|  | Cwt | [7 empty] | @Rs: | 4928.49 | P/Cwt | Rs: | 0 | 15032
15 | Erection and fitting in position of iron trusses staging of water tanks etc:
(G.S.I.No. 3 P/ 90)
| Qty: same as item No: |  |  |  |  | 14 |  |  |  | 0 | Sft.
|  | Sft. | [7 empty] | @Rs: | 271.04 | P/Cwt | Rs | 0 | 827
16 | Supplying and fixing in position iron / steel grill of 3/4"x1/4" size flat iron of
approved design i/c painting 3 coats etc: complete.(weight not to less than
3.7 Lbs/sq: foot of finished grill). (G.S.I. No.26 P/93)
| Window | 3 | x | 3 | x | 4 |  |  |  |  | = | 36 | Sft
|  | Sft | [7 empty] | @Rs: | 180.5 | P/Sft | Rs: | 0 | 6498
Supplying and fixing Z section window ¾” x ¾”x ¾” and partly fixed
i/c designed along with fitting particulars and approved with 3 coats of
glass painting. Etc complete (R.A Approved)
| Window | #REF! | x | #REF! | x | #REF! |  |  | = | #REF! | Sft
| 0 | Sft | [7 empty] | @Rs: | 90.15 | P/Sft | Rs: | 0
Supplying and fixing in position iron steel grill of ¾” x ¼” size flat iron of
approved design i/c painting 03 coats etc complete (weight not to be less
than 3 Lbs/sq: foot of finished grill) (G.S.I. NO.26 P/92)
Window
| 0 | Sft | [7 empty] | @Rs: | 180.5 | P/Sft | Rs: | 0
17 | PAINTING NEW SURFACE
Preparing surface and painting of door and window any type i/c
Edges 3 coats (G.S.I. No.5 P/69)
| Qty: same as item No: |  |  |  |  | 8 |  |  |  |  | = | 12 | Sft
| Qty: same as item No: |  |  |  |  | 8 |  |  |  |  | = | 194.835 | Sft
[12 empty] | 206.835 | Sft
| 206.835 | Sft | [7 empty] | @Rs: | 2116.41 | P%Sft | Rs: | 4377.4766 | 2709
18 | White washing of three coats (G.S.I. No.26 P/53)
| Qtty: of item No. |  |  | 11 | [5 empty] | 0 | Sft
| Ceilling | Qty: same as item No: | [5 empty] | 0 |  |  | = | 0 | Sft
|  | Qty: same as item No: | [5 empty] | 0 |  |  | = | 0 | Sft
[12 empty] | 0 | Sft
| 0 | Sft | [7 empty] | @Rs: | 829.95 | P%Sft | Rs: | 0 | 1693
19 | White washing of One coat (G.S.I. No.26 P/53)
| Qtty: of item No. |  |  |  |  | 11 |  |  |  | 0 | Sft
| 0 | Sft | [7 empty] | @Rs: | 416.63 | P%Sft | Rs: | 0 | 1567
20 | Color Washing (2 coats) (G.S.I.No:25, P/53).
| Qtty: of Item No. |  |  |  |  | 11 |  |  |  | 0 | Sft
| Qtty: of Item No. |  |  |  |  | 12 |  |  |  | 0 | Sft
[10 empty] | 0 | Sft
| 0 | Sft | [7 empty] | @Rs: | 859.9 | P%Sft | Rs: | 0 | 6982
[12 empty] | Total | Rs: | 758893.2342
Cartage of Material
Hill Sand From Bolhari
| 860.6176 | Cft | [7 empty] | @Rs: | #REF! | P%Cft | Rs: | #REF! | 5148
Bajri Shingle from Laki
| 656.3176 | Cft | [7 empty] | @Rs: | #REF! | P%Cft | Rs: | #REF! | 5148
Stone From Amri
| 314.6685 | Cft | [7 empty] | @Rs: | #REF! | P%Cft | Rs: | #REF! | 5148
Bricks 1000 No.
| 14872.2289 | Nos: | [7 empty] | @Rs: | #REF! | P%0Nos: | Rs: | #REF! | 5148
Cement From Zeel Pak Hyderabad
| 191.3805 | Bags | [7 empty] | @Rs: | #REF! | P/Bag | Rs: | #REF! | 5148
Carriage of Earth (Lead 3.0 Mile)
|  | Cft | [7 empty] | @Rs: | 579.41 | P%Cft | Rs: | 0 | 5148
[13 empty] | Rs: | #REF!
[11 empty] | Schedule Items |  | Rs | 758893.2342
[11 empty] | Non Sch: Items |  | Rs | 0
[13 empty] | Rs | #REF!
[9 empty] | Ded: | 0% | below |  | Rs | #REF!
[12 empty] | Net | Rs | #REF!
Assistant Engineer
Public Health Engg: Sub-Divn:I
Larkano
Executive Engineer
Public Health Engg: Dvision-I
Larkano

## S.Mat (hidden)
Material Statement
PUMP HOUSE
S.No: | Item | Qty: | Bajri | Stone | Hill sand | Cement | Bricks
1 | C.C Stone Ballest 1:4:8 | 327.7796 | 0 | 314.6685 | 157.3342 | 31.4668 | 0
2 | C.C. Plain 1:3:6 | 396.015 | 364.3338 | 0 | 182.1669 | 51.4819 | 0
3 | Pacca Brick Work 1:6 | 952.4502 | 0 | 0 | 244.7797 | 32.7643 | 12858.0774
4 | R.C.C Work 1:2:4 | 269.7998 | 237.4238 | 0 | 118.7119 | 47.4848 | 0
5 | C.C Toping 1:2:4 3" thick | 248 | 54.56 | 0 | 27.28 | 10.912 | 0
6 | Dry brick | 380.0286 | 0 | 0 | 0 | 0 | 2014.1516
7 | Cement Plaster 1:6 1/2" Thick | 3258.6221 | 0 | 0 | 130.3449 | 17.2707 | 0
8 | Cement Plaster 1:4 3/8" Thick | 0 | 0 | 0 | 0 | 0 | 0
9 | Cementing Pointing 1:3 | 0 | 0 | 0 | 0 | 0 | 0
| Total |  | 656.3176 | 314.6685 | 860.6176 | 191.3805 | 14872.2289
Assistant Engineer
Public Health Engg: Sub-Divn:
Johi
Assistant Engineer
Public Health Engg: Sub-Divn:I
Larkano
Executive Engineer
Public Health Engg: Dvision-I
Larkano

## C.Wall (hidden)
#REF!
1 | Excavation in foundation of building bridges and other structures.
I/c dag belling dressing refilling around the structures with excavated
Earth watering ramming lead up to one chain and lift up to 5’ (G.S.I. No. 18 P/ 04)
| L/Wall | 2 | x | 100 | x | [5 empty] | = | 200 | Rft
| S/Wall | 2 | x | 75 | x | [5 empty] | = | 150 | Rft
[11 empty] | = | 350 | Rft
Deduction
| Gate Piller | 1 | x | 1 | x | 3 | + | 3 |  |  | = | 6 | Rft |  | 6
| Main gate | 1 | x | 1 | x | 10 |  |  |  |  | = | 10 | Rft |  | 10
[12 empty] | 16 | Rft
| 350 |  |  | - |  | 16 |  |  |  |  | = | 334 | Rft
| 334 |  | x | 1.5 | x | 2 |  |  |  |  | = | 1002 | Cft
|  | 1 | x | 2 | X | 3 | x | 3 | x | 2 | = | 36 | Cft
[11 empty] | = | 1038 | Cft
| 1038 | Cft | [7 empty] | @Rs: | 3176.25 | P%0 Cft | Rs: | 3296.9475
2 | Cement concrete brick or stone ballast 1 ½” to 2” gauge.
(Ratio 1:4:8) (G.S.I No. 4 P/ 17)
| L/Wall | 334 | x | 1.5 | x | 0.5 | [5 empty] | 250.5 | Cft
|  | 1 | x | 2 | x | 3 | x | 3 | x | 0.5 |  | 9 | Cft
[12 empty] | 259.5 | Cft
| 259.5 | Cft | [7 empty] | @Rs: | 9416.28 | P%Cft | Rs: | 24435.2466
3 | Cement concrete plain i/c placing compacting finishing and
curing complete i/c screening and washing of stone aggregate
without shuttering (Ratio 1:3:6) (G.S.I.No 5 P/ 18)
| L/Wall | 334 | x | 1 | x | 4 |  |  |  | = |  | 1336 | Cft
| 1336 | Cft | [7 empty] | @Rs: | 12595 | P%Cft | Rs: | 168269.2
4 | Erection and removal of centering for R.C.C or plain C.C Work
of deodar Wood 1st class(vertical). (G.S.I.No. 18 P/ 19)
| L/Wall O/S | 2 | x | 334 | x | 4 | x |  |  | = |  | 2672 | Sft
| 2672 | Sft | [7 empty] | @Rs: | 3127.41 | P%Sft | Rs | 83564.3952
7 | R.C.C work i/c all labour and material except the cost of steel
reinforcement and its labour for b/b which will be paid separately.
This rate also i/c all kinds of forms moulds lifting, shutting, curing,
rendering and finishing the exposed surface (i/c s/w of shingle) (a) R.C work in
roof slab beams columns rafts lintels and other structural members laid in
situ or prrecast laid in position complete in all respect. (I) Ratio 2:2:4 Lbs
cement2 Cft, sand 4 cft shingle1/8” to ¼” gauge. (G.S.I No. 6 P/ 16).
P/Beam
| Long Wall | 0 | x | #REF! | x | #REF! | x | 1 | = | #REF! | Cft.
| S/Wall | 0 | x | #REF! | x | #REF! | x | 1 | = | #REF! | Cft.
| Gate Piller | 2 | x | 2.5 | x | 2.5 | x | 1.5 |  |  | = | 18.75 | Cft
|  | 2 | x | 2 | x | 2 | x | 2.5 |  |  | = | 20 | Cft
|  | 2 | x | 1.5 | x | 1.5 | x | 7 |  |  | = | 31.5 | Cft
[12 empty] | 70.25 | Cft
| 70.25 | Cft | [7 empty] | @Rs: | 337 | P/Cft | Rs: | 23674.25 |  | 36059
8 | Fabrication of mild steel reinforcement for C.C i/c cutting, bending,
laying in position making joints and fastening i/c cost of binding wire
(also i/c removal of rust from bars).(G.S.I No 8 P/ 16)
| 70.25 | x |  | 4.5 | / | 112 |  |  | = | 2.8225 | Cwt
| 2.8225 | Cwt | [7 empty] | @Rs: | 5001.7 | P/Cwt | Rs: | 14117.5215 |  | 21457
6 | Pacca brick work in other then building i/c stricking of joints upto
20ft height in cement, sand, mortar (1:6) (G.S.I. No 7 P/ 21)
| Length | [10 empty] | 350 | Rft
Deduction
| Gate | 1 | x | 10 | [7 empty] | 10 | Rft
| Piller | 2 | x | 1.5 | + | 1.5 |  |  |  | = |  | 6 | Rft
[12 empty] | 16 | Rft
| 350 |  |  | - |  | 16 |  |  |  |  | = | 334 | Rft
|  | 334 | / | 6.75 | = | 49.4815 |  |  |  |  | Say | 50
| C/Wall | 1 | x | 50 | x | 0.37 | x | 4 |  | = |  | 74 | Cft
| W/Piller | 50 | x | 0.75 | x | 0.37 | x | 4 |  | = |  | 55.5 | Cft
[12 empty] | 129.5 | Cft
| 129.5 | Cft | [7 empty] | @Rs: | 12346.65 | P%Cft | Rs: | 15988.9118
10 | Cement, Plaster (1:6) up to 12’ height ½” thick (G.S.I. No.11 P/58)
|  | 1 | x | 50 | x | 6 | x | 4 |  | = |  | 1200 | Sft
| W/Piller | 50 | x | 1.5 | x | 4 |  |  |  | = |  | 300 | Sft
| Top Wall | 1 | x | 50 | x | 6 | x | 0.37 |  | = |  | 111 | Sft
[12 empty] | 1611 | Sft
| 1611 | Sft | [7 empty] | @Rs: | 2206.6 | P%Sft | Rs: | 35548.326
11 | Cement, Plaster (1:4) up to 12’ height 3/8” thick (G.S.I. No.11 P/58)
| 1611 | Sft | [7 empty] | @Rs: | 2197.52 | P%Sft | Rs: | 35402.0472
12 | Cement, Pointing struck joint on walls (1:3) (G.S.I. No.11 P/57)
| Out side | 1 | x | 334 | x | 4 |  |  | = |  |  | 1336 | Sft
| 1336 | Sft | [7 empty] | @Rs: | 1213.58 | P%Sft | Rs: | 16213.4288
13 | Making and fixing steel grated door with 1/16” thick sheeting angle iron frame 2”x2”x 3/8”
and ¾” sq: bars 4” Center to center with locking arrangement (G.S.I. No.11 P/97)
| Door | 1 | x | 6 | x | 10 |  |  |  | = |  | 60 | Sft
| 60 | Sft | [7 empty] | @Rs: | 726.72 | P/Sft | Rs: | 43603.2
16 | PAINTING NEW SURFACE
Preparing surface and painting of door and window any type i/c Edges 3 coats
(G.S.I. No.5 P/6)
|  | 2 | x | 60 | [5 empty] | = |  | 120 | Sft
| 120 | Sft | [7 empty] | @Rs: | 2116.41 | P%Sft | Rs: | 2539.692
17 | White washing of two coats (G.S.I. No.26 P/55)
| Qtty: of item No. |  |  | 11 | [7 empty] | 1611 | Sft
| Gate Pillers |  |  | 2 | x | 4 | x | 1.5 | x | 7 | = | 84 | Sft
| Plinth of C/W |  |  | 2 | x | 334 | x | 2.5 |  |  | = | 1670 | Sft
[12 empty] | 3365 | Sft
| 3365 | Sft | [7 empty] | @Rs: | 829.95 | P%Sft | Rs: | 27927.8175
18 | Color Washing (2 coats) (G.S.I.No:24, P/60).
| Qtty: of Item No. |  |  | 11 | [7 empty] | 1611 | Sft
| Qtty: of Item No. |  |  | 12 | [7 empty] | 1336 | Sft
[12 empty] | 2947 | Sft
| 2947 | Sft | [7 empty] | @Rs: | 859.9 | P%Sft | Rs: | 25341.253
[12 empty] | Total | Rs: | 519922.2371
15 | Cartage of Material
#REF!
| 942.8015 | Cft | [7 empty] | @Rs: | #REF! | P%Cft | Rs: | #REF! |  | 5148
#REF!
| 1290.94 | Cft | [7 empty] | @Rs: | #REF! | P%Cft | Rs: | #REF! |  | 5148
#REF!
| 249.12 | Cft | [7 empty] | @Rs: | #REF! | P%Cft | Rs: | #REF! |  | 5148
#REF!
| 1748.25 | Nos: | [7 empty] | @Rs: | #REF! | P%0Nos: | Rs: | #REF! |  | 5148
#REF!
| 247.9179 | Bags | [7 empty] | @Rs: | #REF! | P/Bag | Rs: | #REF! |  | 5148
Carriage of Earth (Lead 3.0 Mile)
|  | Cft | [7 empty] | @Rs: | 579.41 | P%Cft | Rs: | 0 |  | 5148
[13 empty] | Rs: | #REF!
[11 empty] | Schedule Items |  | Rs | 519922.2371
[11 empty] | Non Sch: Items |  | Rs | 0
[13 empty] | Rs | #REF!
[9 empty] | Ded: | 0% | below |  | Rs | #REF!
[12 empty] | Net | Rs | #REF!
[5 empty] | For | 1 | x | #REF! |  |  |  | = | Rs: | #REF!
Assistant Engineer
Public Health Engg: Sub-Divn:I
Larkano
Executive Engineer
Public Health Engg: Dvision-I
Larkano

## M.State (hidden)
Material Statement
COMPOUND WALL.
S.No: | Item | Qty: | Bajri | Stone | Hill sand | Cement | Bricks
1 | C.C Stone Ballest 1:4:8 | 259.5 | 0 | 249.12 | 124.56 | 24.912 | 0
2 | C.C. Plain 1:3:6 | 1336 | 1229.12 | 0 | 614.56 | 173.68 | 0
3 | Pacca Brick Work 1:6 | 129.5 | 0 | 0 | 33.2815 | 4.4548 | 1748.25
4 | R.C.C Work 1:2:4 | 70.25 | 61.82 | 0 | 30.91 | 12.364 | 0
6 | Cement Plaster 1:6 1/2" Thick | 1611 | 0 | 0 | 64.44 | 16.11 | 0
7 | Cement Plaster 1:4 3/8" Thick | 1611 |  | 0 | 48.33 | 9.1827 | 0
8 | Cementing Pointiong 1:3 | 1336 | 0 | 0 | 26.72 | 7.2144 | 0
| Total |  | 1290.94 | 249.12 | 942.8015 | 247.9179 | 1748.25
Assistant Engineer
Public Health Engg: Sub-Division
Johi

## BOQ
BILL OF QUANTITY
(A) |  |  |  | Construction of Water Supply scheme Rais Mohammad Khan Chandio UC- Rato Kot Taluka Larkano (ADP 2015-16)
Item # | Quantities | Description and rate of Item to be executed at site | [8 empty] | Rate | Unit | Amount in Rupees
1 | 2 | 3 | [8 empty] | 4 | 5 | 6
PART- 1 TUBE WELL
1 | Boring for tube well in all bearing soil from ground level upto 100' ft: or 30.50 meters depth i/c sinking & with drawing of casing pipe (PHSOI NO.1 P- 41 )
12"dia
| 100 |  | Rft | [6 empty] | @Rs | 743 | P.Rft | Rs | 74300
3"dia Test bore
| 100 |  | Rft | [6 empty] | @Rs | 160 | P.Rft | Rs | 16000
2 | Providing strong substantailly build wooden locked box with compartment for preserving 2 lbs (1 kg) samples of stratas (PHSI NO.5 P-43 ).
| 1 |  | No | [6 empty] | @Rs | 3530 | P.Each | Rs | 3530
3 | Taking & preserving in Box 2 lbs (1 Kg) samples of Strata from bore holes (PHSI NO. 7 P-43)
| 4 |  | Samples | [6 empty] | @Rs | 101 | P.Each | Rs | 404
4 | Taking samples of water from bore holes & placing in two separate bottles (PHSI No.9P-43)
| 4 |  | Samples | [6 empty] | @Rs | 131 | P.Each | Rs | 524
5 | Supplying & Installing PVC strainer B class of approved desing quality & make i/c necessary sockets etc complete (PHSI No.9 P- 43)
8"dia
| 26 |  | Rft | [6 empty] | @Rs | 554.05 | P.Rft | Rs | 14405.3
6 | Supplying & Installing PVC blind pipe (B) class of approved desing quality & make i/c necessary sockets etc complete (PHSI No.12 P- 44)
8"dia
| 76 |  | Rft | [6 empty] | @Rs | 516.8 | P.Rft | Rs | 39276.8
7 | Shrounding with graded Bajri (3/8"to 1/8") in between bore holes & blind pipe for 8" dia the diameters of strainers (PHSI No.13 P- 45)
| 100 |  | Rft | [6 empty] | @Rs | 105 | P.Rft | Rs | 10500
8 | Providing & fixing of PVC end plug of approved quality (PHSI No. 8 P- 43).
| 1 |  | No | [6 empty] | @Rs | 2607 | P.Each | Rs | 2607
[11 empty] | G.Total: |  | Rs | 161547.1
[5 empty] | 161547.1 |  |  | x | 2 |  |  |  | Rs | 323094.2
PART- 2 PUMP HOUSE (12X10)
1 | Excavation in foundation of building bridges and other structures. | [15 empty] | 18 | + | 0.75 | = | 18.75
| I/c dag belling dressing refilling around the structures with excavated | [15 empty] | 12 | + | 0.75 | = | 12.75
Earth watering ramming lead up to one chain and lift up to 5’ (G.S.I. No. 18 P/ 04)
| 195.5 | Cft | [7 empty] | @Rs: | 3176.25 | P%0 Cft | Rs: | 620.9569
2 | Cement concrete brick or stone ballast 1 ½” to 2” gauge.
(Ratio 1:4:8) (G.S.I No. 4 P/ 14)
| 98.74 | cft | [7 empty] | @Rs: | 9416.28 | P%Cft | Rs: | 9297.6349
3 | Cement concrete plain i/c placing compacting finishing and
curing complete i/c screening and washing of stone aggregate
without shuttering (Ratio 1:3:6) (G.S.I.No 5 P/ 15)
| 225 | cft | [7 empty] | @Rs: | 12595 | P%Cft | Rs: | 28338.75
4 | Erection and removal of centering for R.C.C or plain C.C Work
of Partal Wood 1st class(vertical). (G.S.I.No. 19 P/ 17)
| 376 | sft | [7 empty] | @Rs: | 3127.41 | P%Sft | Rs | 11759.0616
5 | Filling Watering and ramming earth in floor with new earth excavated from
out side lead upto 1 chain and lift upto 5' (G.S.I No 22 P- 4)
| 268.13 | Cft | [7 empty] | @Rs: | 3630 | P%0Cft | Rs: | 973.3119
6 | Pacca brick work in ground floor cement, sand, mortar (1:6)
(G.S.I. No 5 P/ 20)
| 323.63 | Cft | [7 empty] | @Rs: | 12674.36 | P%Cft | Rs: | 41018.0313
7 | R.C.C work i/c all labour and material except the cost of steel
reinforcement and its labour for b/b which will be paid separately.
This rate also i/c all kinds of forms moulds lifting, shutting, curing,
rendering and finishing the exposed surface (i/c s/w of shingle) (a) R.C work in
roof slab beams columns rafts lintels and other structural members laid in
situ or prrecast laid in position complete in all respect. (I) Ratio 2:2:4 Lbs
cement2 Cft, sand 4 cft shingle1/8” to ¼” gauge. (G.S.I No. 6 P/ 16).
P/Beam
| Long Wall | 0 | x | #REF! | x | #REF! | x | 1 | = | #REF! | Cft.
| S/Wall | 0 | x | #REF! | x | #REF! | x | 1 | = | #REF! | Cft.
| 94.26 | Cft | [7 empty] | @Rs: | 337 | P/Cft | Rs: | 31765.62
8 | Fabrication of mild steel reinforcement for C.C i/c cutting, bending,
laying in position making joints and fastening i/c cost of binding wire
(also i/c removal of rust from bars).(G.S.I No 8 P/ 16)
| 3.79 | Cwt | [7 empty] | @Rs: | 5001.7 | P/Cwt | Rs: | 18956.443
9 | Providing and laying 3” thick to toping Cement Concrete (1:2:4) I/c surface,
finishing and dividing in to panel (GSI No. 16 P/42)
| 120 | Sft | [7 empty] | @Rs: | 4411.82 | P%Sft | Rs: | 5294.184
10 | Cement, Plaster (1:6) up to 12’ height ½” thick (G.S.I. No.13 P/51)
| 388 | Sft | [7 empty] | @Rs: | 2206.6 | P%Sft | Rs: | 8561.608
11 | Cement, Plaster (1:4) up to 12’ height 3/8” thick (G.S.I. No.11 P/51)
| 388 | Sft | [7 empty] | @Rs: | 2197.52 | P%Sft | Rs: | 8526.3776
12 | Cement, Pointing struck joint on walls (1:3) (G.S.I. No.19 P/52)
| 448 | Sft | [7 empty] | @Rs: | 1213.58 | P%Sft | Rs: | 5436.8384
13 | Making and fixing steel grated door with 1/16” thick sheeting angle iron
frame 2”x2”x 3/8” and ¾” sq: bars 4” Center to center with
locking arrangement (G.S.I. No.24 P/91)
| 28 | Sft | [7 empty] | @Rs: | 726.72 | P/Sft | Rs: | 20348.16
14 | Fabrication of heavy steel work with angles tees, flat iron round iron and sheet iron
for making trsses girders, tanks etc: i/c cutting tanks etc: i/c cutting drilling riveting
handling assembling and fixing but excluding erection in positiion. (CSI- 2, P-91)
Window
| 2.04 | Cwt | [7 empty] | @Rs: | 4928.49 | P/Cwt | Rs: | 10054.1196
15 | Erection and fitting in position of iron trusses staging of water tanks etc:
(C.S.I.No. 3 P/ 91)
Qty: same as item No:
| 2.04 | 0 | [7 empty] | @Rs: | 271.04 | P/Cwt | Rs | 552.9216
16 | Supplying and fixing in position iron / steel grill of 3/4"x1/4" size flat iron of
approved design i/c painting 3 coats etc: complete.
(C.S.I. No.26 P/93)
| 24 | Sft | [7 empty] | @Rs: | 180.5 | P/Sft | Rs: | 4332
Supplying and fixing Z section window ¾” x ¾”x ¾” and partly fixed
i/c designed along with fitting particulars and approved with 3 coats of
glass painting. Etc complete (R.A Approved)
| Window | #REF! | x | #REF! | x | #REF! |  |  | = | #REF! | Sft
| 0 | Sft | [7 empty] | @Rs: | 90.15 | P/Sft | Rs: | 0
Supplying and fixing in position iron steel grill of ¾” x ¼” size flat iron of
approved design i/c painting 03 coats etc complete (weight not to be less
than 3 Lbs/sq: foot of finished grill) (G.S.I. NO.26 P/92)
Window
| 0 | Sft | [7 empty] | @Rs: | 180.5 | P/Sft | Rs: | 0
17 | PAINTING NEW SURFACE
Preparing surface and painting of door and window any type i/c
Edges 3 coats (G.S.I. No.5 P/69)
| 104 | Sft | [7 empty] | @Rs: | 2116.41 | P%Sft | Rs: | 2201.0664
18 | White washing of three coats (G.S.I. No.26 P/53)
| Qtty: of item No. |  |  | 11 | [5 empty] | 0 | Sft
| 174 | Sft | [7 empty] | @Rs: | 829.95 | P%Sft | Rs: | 1444.113
19 | White washing of One coat (G.S.I. No.26 P/53)
Qtty: of item No.
| 388 | Sft | [7 empty] | @Rs: | 416.63 | P%Sft | Rs: | 1616.5244
20 | Color Washing (2 coats) (G.S.I.No:25, P/53).
| 836 | Sft | [7 empty] | @Rs: | 859.9 | P%Sft | Rs: | 7188.764
21 | Providing and fixing C.I manhole cover with framme
i/c cost of material etc: (P.H.S.I-J(i), P-35) Size 2'x2'
| 0 | Cwt. | [7 empty] | @Rs: | 6985 | P/Cwt. | Rs: | 0
22 | Supplying R.S.J channel section 8"x4" Girders.
(Sch: of Sant: I-141, P-80)
|  | 1 | x | 11.5 | x | 14 | / | 112 | = | 1.4375
| 0 | Cwt. | [7 empty] | @Rs: | 3575 | P/Cwt. | Rs: | 0
[12 empty] | Total | Rs: | 218286.4865
|  |  | 2 Nos | Pump house |  | 218286.4865 |  |  | x | 2 |  |  | Rs. | 436572.973
Part- 3 P.E Pipe Distt: system
1 | Excavation for pipe line entrenches and pits in soft soils i/c trimming and dressing sides to true
alignment and shape leveling of beds of trenches to correct level and grade cutting joint holes
and disposal of surplus earth within a one chain as directed by Engineer incharge providing fence
guards lights flags and temporary crossing for non vehicular traffic where were required lift upto
5ft and lead upto one chain.(P.H.S.I-1, P-60).
| 24450 |  | Cft | [6 empty] | @Rs | 3600 | P%0Cft | Rs | 88020
2 | Providing laying & fixing in trench i/c fitting jointing and testing etc:
complete in all respect the high density polythylene PE pipes
(HDPE-100) for W/S confirming ISO 4427/DIN8074/8075
B.S 3580 & PSI 3051. (P.H.S.I-1, P-25). PN 08.
| 3"dia | 2575 | Rft | [6 empty] | @Rs | 148 | P-Rft | Rs: | 381100
| 4"dfia | 1500 | Rft | [6 empty] | @Rs | 224 | P-Rft | Rs: | 336000
3 | HDPE (PE100) fittings (PH.Sch: of Mat: Item No:1, P-18)
Elbow / Bend 45 Degree
| 3"dia | 20 | Nos: | [6 empty] | @Rs | 894 | P-Each | Rs: | 17880
| 4"dfia | 2 | Nos: | [6 empty] | @Rs | 1324 | P-Each | Rs: | 2648
4 | Elbow / Bend 90 Degree
| 3"dia | 30 | Nos: | [6 empty] | @Rs: | 1118 | P-Each | Rs: | 33540
| 4"dfia | 4 | Nos: | [6 empty] | @Rs: | 1655 | P-Each | Rs: | 6620
4 | HDPE (PE100) fittings (PH.Sch: of Mat: Item No:1, P-19)
Equal tee
| Size (3"x3"x3") | 8 | Nos: | [6 empty] | @Rs | 1676 | P-Each | Rs: | 13408
| Size (4"x4"x4") | 2 | Nos: | [5 empty] | @ | Rs | 2483 | P-Each | Rs | 4966
Un-Equal tee
| Size (4"x4"x3") | 3 | Nos: | [5 empty] | @ | Rs | 3754 | P-Each | Rs | 11262
5 | But fusion joint (PH.Sch: of Mat: I-H, P-20)
| 3"dia | 50 | P-Each | [6 empty] | @Rs | 800 | P-Each | Rs: | 40000
| 4"dfia | 10 | P-Each | [6 empty] | @Rs | 1000 | P-Each | Rs: | 10000
6 | Refilling the excavated stuff in trenches 6” thick Layer i/c watering ramming to
full compaction etc complete (P.H.S- I-24 P-77)
| 22005 |  | Cft | [6 empty] | @Rs: | 2760 | P%0Cft | Rs: | 60733.8
[13 empty] | Rs | 1006177.8
PART- 4 P.E Pipe Rising main
1 | Excavation for pipe line entrenches and pits in soft soils i/c trimming and dressing sides to true
alignment and shape leveling of beds of trenches to correct level and grade cutting joint holes
and disposal of surplus earth within a one chain as directed by Engineer incharge providing fence
guards lights flags and temporary crossing for non vehicular traffic where were required lift upto
5ft and lead upto one chain.(P.H.S.I-1, P-60).
4" dia (110mm)
| 2700 |  | Cft | [6 empty] | @Rs | 3600 | P%0Cft | Rs | 9720
2 | Providing laying & fixing in trench i/c fitting jointing and testing etc:
complete in all respect the high density polythylene PE pipes
(HDPE-100) for W/S confirming ISO 4427/DIN8074/8075
B.S 3580 & PSI 3051. (P.H.S.I-1, P-25). PN 08.
| 4" dia (110mm) | 4500 | Rft | [6 empty] | @Rs | 224 | P-Rft | Rs: | 1008000
3 | HDPE (PE100) fittings (PH.Sch: of Mat: Item No:1, P-18)
Elbow / Bend 45 Degree
| 4" dia (110mm) | 2 | Nos: | [6 empty] | @Rs | 1324 | P-Each | Rs: | 2648
Elbow / Bend 90 Degree
| 4" dia (110mm) | 3 | Nos: | [6 empty] | @Rs: | 1655 | P-Each | Rs: | 4965
4 | HDPE (PE100) fittings (PH.Sch: of Mat: Item No:1, P-19)
Equal tee
| Size (4"x4"x4") | 2 | Nos: | [5 empty] | @ | Rs | 2483 | P-Each | Rs | 4966
5 | But fusion joint (PH.Sch: of Mat: I-H, P-20)
| 4" dia (110mm) | 8 | P-Each | [6 empty] | @Rs | 1000 | P-Each | Rs: | 8000
6 | Refilling the excavated stuff in trenches 6” thick Layer i/c watering ramming to
full compaction etc complete (P.H.S- I-24 P-77)
| 24300 |  | Cft | [6 empty] | @Rs: | 2760 | P%0Cft | Rs: | 67068
[13 empty] | Rs | 1105367
Part - 5 L.S.R
1 | Excavation in foundation of bulding bridge and other structures
I/C dig billing dressing refilling aroud the structures with exavated
Earth wtering ramming up to 5ft (b) in ordinary soil ( G.S.I-18/P/4)
| Qty | 168.45 |  | cft | [5 empty] | @Rs: | 3176.25 | P%0Cft | Rs: | 535.0393
2 | Cement Coancret plain i/c placing compactiong finishing
and curing complete i/c screening and washing of stone
aggregate without shuttering (Ratio 1:4;8)(G.SI-5 P/17
| Qty | 116.76 |  | cft | [5 empty] | @Rs: | 11288.75 | P%Cft | Rs: | 13180.7445
3 | Cement Coancret plain i/c placing compactiong finishing
and curing complete i/c screening and washing of stone
aggregate without shuttering (Ratio 1:2;4)(G.S.I-5 P/15
| Qty | 54 |  | cft | [5 empty] | @Rs: | 14429.25 | P%Cft | Rs: | 7791.795
4 | Pacca Brick Work in foundation and plinth in cement
sand mortar ( 1:6)( G.S.I NO. 4 P/ 20)
| Qty | 170.83 |  | cft | [5 empty] | @Rs: | 11948.36 | P%Cft | Rs: | 20411.3834
5 | Filling watering ramming earth under floor with surplus excavated
earth from out side lead upto one chain and lift upto 5ft (G.S.I-21 P-4)
| Qty | 91.4 |  | cft | [5 empty] | @Rs: | 1512.5 | P%oCft | Rs: | 138.2425
6 | Cement Plaster (1:4) Up to 12 height 1/2'' thick (GSI-ll / P/51)
| Qty | 254.21 |  | sft | [5 empty] | @Rs: | 2293.93 | P%sft | Rs: | 5831.3995
7 | RCC work i/c all labour and material except the cost of steel
reinforecment and its labour for bending and binding which will
be paid separatelu This rate also incluses all kinds of forms moukds
lifiting shuttering curing recdering and finidhing the exposed surface
i/c sceening and washing of shingle ( a) R.C work in roof slab members
laid in site or prreacast laid in position complete in aresplete in respect (i)
Ration 1:2:4 90 lbs cement 2 cft sand 4 cft shingle 1/8'' to 1/4 gayge
GSI-6 P/16)
| Qty | 170.83 |  | cft | [5 empty] | @Rs: | 337 | P.Cft | Rs: | 57569.71
8 | Fabrication of mild steel reinforcement for cement concrete i/c
curring bending laying in position making joints and fastening i/c
cost of binding wire also inclidudes removal for rust from bars
( GSI-8 (II) (a) P/16)
| Qty | 11.08 |  | cwt | [5 empty] | @Rs: | 5001.7 | P.Cwt | Rs: | 55418.836 | P/Cft |  |  |  | Rs. | 55403
9 | Providing Construction joints in concret work of 9'' (225 mm)
made corrugated P.V.C water stop ( with bulb) i/c soldering cost
of material and labour (PHSI -2 P/56)
| Qty | 54.95 |  | Rft | [5 empty] | @Rs: | 86 | P.rft | Rs: | 4725.7 | P/Rft |  |  |  | Rs. | 4726
10 | Cement Plaster (1:4) Up to 12 height 1/2'' thick (GSI-ll / P/51)
| Qty | 200.96 |  | Sft | [5 empty] | @Rs: | 3015.76 | P%sft | Rs: | 6060.4713 | P%Sft |  |  |  | Rs. | 6060
11 | Supply of Dampo ( sch: of Mat: 1-46,P-4
Inside wall & Bed
|  | 3.83 |  | KG | [5 empty] | @Rs: | 125 | P.kg | Rs: | 478.75 | P%Sft |  |  |  | Rs. | 478
12 | Providing G.I pipes Special and clemp etc i/c fixing culting & fitting complete with and i/c the cost of breaking through walls and i/c of making good etc painting two Costs of after cleaning the pipe etc: with white xink paints with pig ment te match the coulors of the building and testing with water to apessure lead head 200 ft- and handling (P.H.S No:1 P-No-12)
| 3/4"dia | 6 |  | Rft | [5 empty] | @Rs: | 62.38 | P.rft | Rs: | 374.28 | P%Sft |  |  |  | Rs. | 478
|  | 23 |  | Rft | [5 empty] | @Rs: | 304.02 | P.rft | Rs: | 6992.46 | P%Sft |  |  |  | Rs. | 478
13 | Providing and fixing M.S 3'' dia flanged made out of M.S steel 3/8'' thick
( Based pm sch rate)
| 3"dia | 8 |  | Nos | [5 empty] | @Rs: | 500.89 | P.Each | Rs: | 4007.12 | P%Sft |  |  |  | Rs. | 478
14 | Supplying and Fixing in position brass bib cock 3/4'' dia standared pattern
(Sant: Sch: 5 P-18)
| 3/4'' dia | 4 |  | Nos | [5 empty] | @Rs: | 348 | P.cwt | Rs: | 1392 | P.Each |  |  |  | Rs. | #VALUE!
15 | C.I Bend with flanged ends with holes i/c turning facing
flanged for all size (P.H.S(M) 1-8 P-11)
|  | 0.58 |  | cwt | [5 empty] | @Rs: | 6096 | P.cwt | Rs: | 3535.68 | P%Sft |  |  |  | Rs. | 478
16 | Cost iron speecials for A.C pressure pipe of class B A CIL ( PHS(M) 1 VII P-16
|  | 1 |  | No | [5 empty] | @Rs: | 375 | P.cwt | Rs: | 375 | P%Sft |  |  |  | Rs. | 478
17 | Jointing C.I M.S flanged pipe and specials flanged and inside a
tremcj i/c supplying rubber paching of the required thichness nuts
bolts with washers etc and other looks required for jioting and testing the
Jointing to the specified pressure etd commplete (PHSI 1 p- 40)
| 3"dia | 6 |  | Nos | [5 empty] | @Rs: | 499 | P.Jt | Rs: | 2994 | P%Sft |  |  |  | Rs. | 478
18 | Providing C.I Main hole cover & frame i/c cost of material etc
(PHSI J (I) P-35_ Size 2x2 = 1 No
|  | 0.5 |  | cwt | [5 empty] | @Rs: | 6985 | Each | Rs: | 3492.5 | P%Sft |  |  |  | Rs. | 478
19 | C.I Sluce valve geavy patte test pessure 21 kg/sq: cm or 300 lbs/sq: inch
| 3"dia | 1 |  | No | [5 empty] | @Rs: | 4290 | P.Each | Rs: | 4290 | P%Sft |  |  |  | Rs. | 478
20 | P/F CI Venttilator weigh not be less than 80 lbs/ each tank roof
of approved design rain with rater right joints i/c painting etc: complete (PHSI 4 P55
|  | 1 |  | No | [5 empty] | @Rs: | 4870 | P.Each | Rs: | 4870 | P%Sft |  |  |  | Rs. | 478
[17 empty] | Total |  | Rs: | #VALUE!
[12 empty] | Total: | Rs | 230468
[5 empty] | 230468 |  |  | x | 2 |  |  |  | Rs | 460936
PART- PUMPING MACHINERY (N/S)
1 | Supplying installing in position i/c transportation at site of work HMA stainless steel deep well turbine pump Type BP 17-6 ,7.50 BHP siemens motor 3 phase 400 volts, 50 HZ ,2900 rpm 2 pi;es with suction discharge top set 3"outlet with mechnbical seal, bowl assembly 3"dia coloumn pipe assembly 3"dia x2.7 mx 6 Nos. capable giving discharge 70 gpm against the head of 160 ft: and pump setting depth 55 ft: i/c motor arrangement control unit (7.50 BHP 7.46 KW ASD i/c earthing 0.6Mx0.6Mx3.6mm (2"x2"x1/4") G.I plate burried in the depth of 3.70 m or 12 ft: as per PWD specifications and providing fixing motor control unit consisting metallic box , circut breaker amper meter, volts meter, magnatic conductor, on/off switch, electronic over current relay and indications lamps i.c providing internal electric wiring for main and testing the pumping set agains t72 hours etc complete.(R.A)
| 7.50 BHP | 2 | sets | [6 empty] | @Rs | 1056381 | P.Set | Rs: | 2112762 | @Rs | 0
b) | Inter Connection
1 | Providing laying G.P pipe and cla,mps etc i/c fixing cutting and fitting complete i/c cost of breaking through walls and making good etc paintng 3 coats after cleaning the pipe with zink paint with pigments to match the pressure head of 200 ft: and ha ndling (SSI No.1 P-12)
Delivery line 3" dia
| 40 | Rft | [7 empty] | @Rs | 360.4 | P.rft | Rs: | 14416
2 | Providing & fixing M.S flanges 3" dia made out of M.S 3/8"thick cutting drilling holes etc complete R.A approved
Delivery line 3" dia
| 8 | Nos | [7 empty] | @Rs | 589 | P.Each | Rs: | 4712
3 | C.I bend with flanges ends with holes i/c turning and facing of flanges for all sizes ( PHS OF mat No. 8 P- 11)
Delivery line 3" dia
| 0.26 | cwt | [7 empty] | @Rs | 6096 | P.cwt | Rs: | 1584.96
6 | C.I tapper flate bottomed or central tampered flanges end with holes i/c turning
facing flange for all sizes (P.H.S (M) I No 7 P/ 11)
Reduder 4x3
| 0.53 | cwt | [7 empty] | @Rs | 6096 | P.cwt | Rs: | 3230.88
7 | Reflex valve heavy pattern test pressure 21 kg /sq, cm or 300 lbs /sq inch
(P.H.S (M) I No C P/ 11)
| 2 | Nos | [7 empty] | @Rs | 1543.75 | P.cwt | Rs: | 3087.5
8 | Jointing C.I/M.S flanged and specials pipes and inside a trenches i/c
supplying of the rubber packing of the required thickness nuts bolts
and washers etc and other tools required for jointing and testing the
joints in the specified pressure etc complete (P.H.S I No 1 P/ 40)
3"dia
| 16 | Nos | [7 empty] | @Rs | 499 | P.Jt | Rs: | 7984
[12 empty] | G.Total: | Rs. | 35015.34
General Abstract
| S.# | Sub- Works |  |  |  | Schedule Amount |  |  |  |  | N/S Amount |  | G.Total:
| 1 | Tube wells (2 Nos) |  |  |  | 323094.2 |  |  |  |  | 0 |  | Rs | 323094.2
| 2 | Pump House |  |  |  | 436572.973 |  |  |  |  | 0 |  | Rs | 436572.973
| 3 | P.E pipe Distt:system |  |  |  | 1017808 |  |  |  |  | 0 |  | Rs | 1017808
| 4 | P.E pipe R/main |  |  |  | 1210129 |  |  |  |  | 0 |  | Rs | 1210129
| 5 | L.S.R (2 Nos) |  |  |  | 460936 |  |  |  |  | 0 |  | Rs | 460936
| 6 | Pumping Machinery |  |  |  | 36260 |  |  |  |  | 2112762 |  | Rs | 2112762
|  | G.total: |  |  |  | 3484800.173 |  |  |  |  | 2112762 |  | Rs | 5561302.173 | [7 empty] | *
Amount Total (a)
| ---------------- % above /below on the rates CSR | [8 empty] | Amount to be added /deducted on the
basis of premium quoted. TOTAL(b)
Total (A) = a+b in words & figure:
| CONTRACTOR | [8 empty] | Executive Engineer
Public Health Engg:Division-I
Larkano