## Pumping Machinery
SCHEDUEL "B"
NAME OF WORK:- Supply and Installation of Pumping Machinery for Pumping Station Aliabad Hyderabad. (Work No. 13)
Part "A" (Non Schedule Items)
S-No | Items | Quantity | Unit | Rate | Amount
1 | Supply, Installation, testing and commissioning of KSB Non clogging pump TYPE KWPz 100-400, 500 IGPM, 100ft Head including 40BHP Electric motor, 1455 RPM, 3PH/50Hz mounted on common base steel frame including foundation bolts and Motor Control unit with all accessories and errection etc complete in all respects as per directions of engineer incharge. (RA Attached) | 2 | Job
2 | Supply, Installation, testing and commissioning of KSB Non clogging pump TYPE KWPz 200-400, 1400 IGPM, 100ft Head including 75BHP Electric motor, 1455 RPM, 3PH/50Hz mounted on common base steel frame including foundation bolts and Motor Control unit with all accessories and errection etc complete in all respects as per directions of engineer incharge. (RA Attached) | 1 | Job
3 | Supply & Installation of control cable for motors 4 core 35/50mm square including 2" dia pvc conduit, sockets, bends and cutting of floor etc complete in all respects as per instruction of engineer (RA Attached) | 250 | P-Rft
4 | Supply & Installation 4 core 120mm square main cable from transformer to Main Control Unit (MCU) etc complete in all respects as per instruction of engineer (RA Attached) | 100 | P-Rft
5 | Providing and fixing plate type earth electrode 24" x 24" x 3mm including 50mm dia GI pipe , 2 x 70 sq mm bare copper conductor including 12" x 2" x 6mm copper plate for earth connecting point & inspection chamber 18" x 18" with cover detail shown in drawing etc complete (RA Attached) | 1 | Job
6 | Providing and fixing 6.4mm thick M.S suction & delivery pipes etc complete in all respects as per instructions of engineer incharge. (RA Attached)
| a) 8" dia | 200 | P-Rft
| b) 6" dia | 100 | P-Rft
7 | Providing and fixing 45o/90o C.I flanged Bends etc complete in all respects as per instructions of engineer incharge. (RA Attached)
| a) 8" dia (weight not less than 40 kg) | 5 | Each
| b) 6" dia (weight not less than 25 kg) | 10 | Each
8 | Providing and fixing 6" / 8" dia Heavy duty Sluice valve etc complete in all respects as per directions of engineer incharge. (RA Attached) | 5 | Each
9 | Providing and fixing 6" / 8" dia Heavy duty Non Return Valve etc complete in all respects as per directions of engineer incharge. (RA Attached) | 5 | Each
10 | Providing and fixing 6" / 8" dia Foot Valve etc complete in all respects as per directions of engineer incharge. (RA Attached) | 5 | Each
11 | Providing and fixing 8" dia Flanges etc complete. | 20 | Each
12 | Providing and fixing 6" dia Flanges etc complete. | 20 | Each
13 | Providing flanged joints to pipes and specials including cost of nut bolts & rubber packing etc complete in all respects as per directions of engineer incharge.
| a) 6" dia | 30 | Joint
| b) 8" dia | 20 | Joint
| c) 18" dia | 6 | Joint
14 | Providing and fixing 24" x 6" C.I flanged Reducer etc complete in all respects as per directions of engineer incharge. (RA Attached) | 1 | Each
15 | Providing and fixing 24" x 8/6" x 24" C.I flanged Tee including dressing coupling etc complete in all respects as per directions of engineer incharge. | 4 | Each
16 | Providing and fixing 24" C.I short piece with flanges including cost of nut bolts etc complete in all respects as per directions of engineer incharge. | 1 | Each
17 | Providing and fixing 24" dia 45 / 90 C.I flanges bends etc compelet in all respects as per directions of engineer incharge. | 1 | Each
18 | Construction of Pumps foundation in Ratio 1:2:4 Plain Cement Concrete as per pumps manufacturer's requirement etc compete. RA Attached. | 2 | Each
19 | Supplying and installing Donkey pump 1/2 HP including providing power plug, service wire, 1-1/4" dia PVC pipe 60ft deep tube well for priming of pumps and 10ft 1-1/4" dia G.I pipe etc complete in all respects as instructions of engineer incharge. (RA Attached) | 1 | Job
20 | Providing and fixing 6.4mm thick M.S 24" dia manifold pipe, connection 710 MM etc complete in all respects as per instructions of engineer incharge. | 100 | Rft
| a) 24" dia |  |  | Part "A" Total Rs.
1 | Total Amount of Schedule Item Part "A" | Rs.
2 | I the Contractor M/S _____________________________________
Here by quote__________% premium the
| above / below the Schedule Items. | Rs.
3 | Total Amount of Non Schedule Items
| Part "B" in | Rs.
| Total Tender Amount 1 to 3 (in figures) | Rs.
In word: _________________________________________________________
_______________________________________________________________________________________