SCHEDULE B 	PROVIDING INSTALLING AND TESTING PUMPING MACHINERY 50 BHP (3 SETS) I/C SUCTION & DELIVERY FOR URBAN WATER SUPPLY SCHEME PHASE-II JHOL CITY DISTRICT SANGHAR.

| S.# | Description | Qty | Rate | Unit | Amount |
| --- | --- | --- | --- | --- | --- |

- Supplying installing and testing in position i/c transportation at site of work Water Supply Scheme Phase-II Jhol City electric pumping sets consisting of AC Electric Motor 50.0 BHP 3phase 50 cycle 400/420 volts of 960 RPM Siemens made (Type 1601 coupled with non clogging pump Type KWPZ 80-400 size 4’x3” mounted on common base steel frame or base plate capable of discharge 620 gallons per munite against  a head of 160 ft i/c installing of pumping set on cement concrete foundation nuts and bolts of 5/8” dia to embed in cc foundation i/c providing motor contril Unit MCU consists of circuit breakers magnetic i/c conductor over level protection under/over voltage protection phase failure protection of meter with current transformer volts meter with potential transformer automatic star delta charge over switch control and powers cables indicating lights and all these components are fixed in a automatic duct and smoke proof box i/c providing internal electric wiring for main with 3-7 /0.44 PVC insolated wire 660 volts  grade in 1” (25mm) PVC conduct on surface as required i/c P/F ear thing etc with (2’x2’x1/4’)(0.6x0.6x6.25 mm)G.I Plate buried in the ground at a depth of 12’ (3.7m) or less as per Pak P.W.D specification and testing of pumping  set against a head of 72 hour sets complete. (R.A Attached).

3 Set.				Rs:  632040/-		P/Set.	          Rs. 1896120/-

2.	Manufacturing installing M.S pipe 4”dia made out MS sheet 3/18’ thick i/c cutting folding proper curvature shape welding etc complete.(Approved based on scheduel)

Suction pipe.

4” DIA

66.0 Rft.			Rs. 506/60		P/Rft.		Rs. 33436/-

Delivery Pipe

20.0 Rft.			Rs. 1475/05		P/Rft.		Rs. 29501/-

3.	M/I and furnishing M.S flanged 3/8” thick M.S sheet of required size drilling holes i/c cutting bending to correct shape welding etc complete. (R.A Attached)

12”dia

8.0 Nos:			Rs.1522/94		Each.		Rs: 12184/-

3” dia

12.0 Nos:			Rs.500/89		Each.		Rs: 6011/-

4.	C.I Tee flanged end with hoile i/c turning and facing flanges (PHSMI No.    P/           )

12”x12”x3”

2.95 Cwt			Rs. 6096/-		P/Cwt		Rs. 17983/-

5.	C.I Bend with flanged end with holes i/c turning and facing of flanges for all Sizes (P.H.S.I.No: 8 P-11).

4.92 Cwt			Rs: 6096/-		P/Cwt.		Rs: 29992/-

7.	C.I Foot valve heavy pattern with cone type gate imported. (S.O..M.I.No: 4 P/16)

12”Dia.  3.0 Nos:		Rs.893/75		Each.		Rs.2681/-

7.      	C.I Sluice valve heavy pattern (test pressure) 21 kg per sq: or 300 lbs/sq: inch (P.H.S.I.No: 1 P/9)

12”Dia.  1x 3.	3.0 No:		Rs.4290/-		Each.			Rs. 12870/-

8.      	C.I Reflex valve heavy pattern (test pressure) 21 kg per sq: or 300 lbs/sq: inch (P.H.S.I.No: 1 P/9)

12”Dia.  1x 3.	3.0 Nos:	Rs.1543/75		Each.			Rs. 4631/-

9.	Jointing C.I M.S flanged pipe and specials flanged and inside a trenches nuts and bolts with washer etc and other is required for jointing and testing joints to the specified pressure etc complete. (P.H.S.I.No: 1 P/40)

12”Dia.	1x10=10 Joints.		Rs.513/-		P/Joint.			Rs. 22390/-

3”Dia.	1x21=21 Joints.		Rs.499/-		P/Joint.			Rs. 10479/-

Total:-	Rs. 2078278/-

CONDITIONS.

- Any error omission in the specification quantity and unit will be governed by the relevant schedule items.

- The rates should be inclusive of all taxes i.e sales tax octori tax etc.

- No separate carriage will be paid to the contractor

- No premium will be allowed for no-schedule items.

- The decision of the Superintending Engineer, Public Health Engineering Circle Mirpurkhas will be final and binding the parties if in any dispute.

EXECUTIVE ENGINEER

PUBLIC HEALTH ENGG: DIVISION

SANGHAR