## Overall Summary
OVERALL SUMMARY OF COST ESTIMATE FOR
INTERNAL & EXTERNAL ELECTRICAL WORKS OF
GIRLS HOSTEL
Sr. No. | Description | Amount (Rs.)
1. | Internal Electrification | Rs.
2. | External Electrification | Rs.
TOTAL |  | Rs.
Contractor
Project Director

## Internal Elect.
COST ESTIMATE FOR
INTERNAL ELECTRICAL WORKS OF
GIRLS HOSTEL
SINDH COLLEGE OF ART AND DESIGN SUKKUR
S.No. | ITEM DESCRIPTION | QTY. | UNIT | UNIT RATE (Rs) | TOTAL AMOUNT (Rs)
1. | Wiring for light or fan point with 2-1.5mm² PVC insulated cable +1-1.5mm² E.C.C in 20mm dia (3/4") PVC conduit recessed in wall or column as required.( SI # 124 Page # 015) | 1201 | Nos. | 1130 | 1357130
2. | Wiring for two way light point with 2-1.5mm² PVC insulated cable +1-1.5mm² E.C.C in 20mm dia (3/4") PVC conduit recessed in wall or column as required. | 18 | Nos. | 703.9 | 12670.2
3. | Wiring for plug point with 2-1.5mm² S/C, PVC insulated cable in 20mm dia (3/4") PVC conduit recessed in the wall or column as required.( SI # 126 Page # 15) | 171 | Nos. | 985 | 168435
4. | Wiring for mains with 2-2.5mm² S/C, PVC insulated cable in 25mm dia (1") PVC conduit recessed in the wall or as required. (Lighting Circuit) ( SI # 10 Page # 02) | 14000 | Rft. | 67 | 938000
5. | Wiring for mains with 2-4mm² S/C, PVC insulated cable in 25mm (1") dia PVC conduit recessed in the wall or as required.(Power Circuit) ( SI # 11 Page # 02) | 1600 | Rft. | 76.21 | 121936
6. | Providing & fixing of one way, S.P., 5A, flush type switch on a given prepard board. ( SI # 219 Page # 33) | 805 | Nos. | 54 | 43470
7. | Providing & fixing of two way, S.P., 5A, flush type switch on a given prepard board. (Sl # 220 Page # 33) | 36 | Nos. | 55 | 1980
8. | Providing and fixing of flush type, 2/3 pin, 5 Amps, S.P., plug socket, switch and shoe unit on a given prepared board. ( SI # 226 Page # 33) | 290 | Nos. | 151 | 43790
9. | Providing, fixing and connecting of flush type, 3 pin, 15A, S.P., plug socket, switch and shoe unit on a given prepared board. ( SI # 227 Page # 33) | 25 | Nos. | 162 | 4050
10. | Providing and fixing of metal board, recessed in the wall or columns and covered with socket sheet to house plug-socket switch or regulator etc.( SI # 04 Page # 13) | 1156 | Sqft. | 675.606 | 781000.536
11. | Providing and fixing of metal board to accommodate mains or sub mains switches, plug socket units etc., recessed in the wall, as required. ( SI # 03 Page # 13). | 150 | Sqft. | 750.448 | 112567.2
COST OF PART 'I' |  |  | (Rs.) |  | 3585028.936
PREMIUM ___________ Above / Below |  |  | (Rs.)
3585028.936
TOTAL COST OF PART 'I' |  |  | (Rs.) |  | 0
S.No. | ITEM DESCRIPTION | QTY. | UNIT | UNIT RATE (Rs) | TOTAL AMOUNT (Rs)
1. | Providing, installing, fixing and connecting of following light fixtrues with lamps, chokes, starters, capacitors etc., complete with all internal connections and all fixing and mounting accessories. Jobs includes rod and wiring as given in drawing.
1.1 | Philips make or equivalent light fitting TMS-140 with 1x36 W 'T5' fluorescent lamps, complete in respect with all accessories. | 200 | Nos. |  | 0
1.2 | Phillips make or equivalent Ceiling light fixture with 11W LED lamp, complete in all respect with all accessories. To be approved by Client. | 156 | Nos. |  | 0
0
1.3 | Phillips make or equivalent Ceiling cylender light fixture with 12 -15 W sever lamp, complete in all respect with all accessories. To be approved by Client. | 200 |  |  | 0
2. | Providing, installing and connecting of following fans:
2.1 | Millat make 56" sweep ceiling fan complete with fan dimmer, canopy, down rod, etc. including fixing of fan dimmers and making holes on both sides of down rod and wiring it with 1.5mm² twin core., 450/750V grade PVC/PVC + 1-1.5mm² ECC cable, etc. and also providing of 16mm dia mild steel fan hook on RCC roof or beam as required ,complete in all respects with all accessories. | 200 | Nos. |  | 0
2.2 | Millat make or equivalent 8" sweep exhaust fan, complete with capacitors including making of hole in wall to accommodate the fan & repairing good the damages. | 15 | Nos. |  | 0
2.3 | Same as Item 2.2 above but Millat make or equivalent 12" sweep exhaust fan. | 34 | Nos. |  | 0
| TOTAL COST OF SECTION "B" |  | (Rs.) |  | 0
Contractor
Project Director
Section "C" Distribution Boards & Feeders
S.No. | ITEM DESCRIPTION | QTY. | UNIT | UNIT RATE (Rs) | TOTAL AMOUNT (Rs)
1. | Providing, installing, connecting & commissioning of the following Distribution Boards (DBs) fabricated of 14 SWG steel clad, cubical design with hinged door cover, wall (recessed) mounted, factory assembled, suitable for 3 phase, 4 wire, 500 volts, 50 Hz A.C. Power Supply complete with copper cable lugs, glands, neutral link, earth block, terminal block etc., & having following configurations. (All equipment rated to 7.5 kA short circuit rating and 50°C ambient temperature at 415V). Panel enclosure to comply with IP-50.
1.1 | LPDB GF-1 & GF-2
Short Circuit Rating 7.5kA
Incoming
1 -63 A, T.P., M.C.C.B
3 - Phase (R.Y.B) indication lamps.
Outgoing
9 - 15 A, S.P., M.C.B.s
| 33 - 10 A, S.P., M.C.B.s | 2 | No. |  | 0
1.2 | LPDB GF 3
Short Circuit Rating 7.5kA
Incoming
1 -100 A, T.P., M.C.C.B
3 - Phase (R.Y.B) indication lamps.
Outgoing
12 - 15 A, S.P., M.C.B.s
| 30 - 10 A, S.P., M.C.B.s | 1 | No. |  | 0
12 - 20 A, S.P., M.C.B.s
1.3 | LPDB FF2
Short Circuit Rating 7.5kA
Incoming
1 -63 A, T.P., M.C.C.B
3 - Phase (R.Y.B) indication lamps.
Outgoing
12 - 15 A, S.P., M.C.B.s
| 39 - 10 A, S.P., M.C.B.s | 1 | No. |  | 0
1.4 | LPDB FF1, SF1, SF2
Short Circuit Rating 7.5kA
Incoming
1 -63 A, T.P., M.C.C.B
3 - Phase (R.Y.B) indication lamps.
Outgoing
6 - 15 A, S.P., M.C.B.s
| 36 - 10 A, S.P., M.C.B.s | 3 | No. |  | 0
2. | Providing, laying & connecting of PVC/PVC 600/1000V grade copper conductor cable from Main Distribution Board (MDB) to the respective Distribution Boards (DBs), recessed in the RCC or on surface / concealed in wall or column as required, complete in all respect with all fixing and termination accessories and entire satisfaction of Consultant / Owner.
2.1 | DB- GF1, GF2
| 16mm², 4Core, PVC/PVC + 10mm² ECC in 38mm dia rigid PVC conduit in ground / floor as required from MDB. | 200 | Rft. |  | 0
2.2 | DB- GF 3
| 35mm², 4Core, PVC/PVC + 16mm² ECC in 75mm dia rigid PVC conduit in ground / floor as required from MDB. | 135 | Rft. |  | 0
2.3 | DB- FF1, SF1 & SF2
| 16mm², 4Core, PVC/PVC + 10mm² ECC in 38mm dia rigid PVC conduit in ground / floor as required from MDB. | 350 | Rft. |  | 0
2.4 | DB- FF2
| 16mm², 4Core, PVC/PVC + 10mm² ECC in 38mm dia rigid PVC conduit in ground / floor as required from MDB. | 130 | Rft. |  | 0
TOTAL COST OF SECTION "C" |  |  | (Rs.) |  | 0
Contractor
Project Director
S.No. | ITEM DESCRIPTION | QTY. | UNIT | UNIT RATE (Rs) | TOTAL AMOUNT (Rs)
1. | Providing, making and testing of earth points with 2' x 2' x 1/8" thick copper plate buried 5 meter deep or to the depth of permanent water level whichever is less covered with charcoal and lime in specified ratio confirming to specification and drawing. | 2 | Job |  | 0
2. | Providing, drawing, connecting & testing of 2-70mm² bare copper conductor as earthing leads in 32mm dia G.I. pipe burried in ground or connected in R.C.C. or masonary as requried from Panel Board to the earth plate including making of 18"x18" cement concrete chamber duly plastered and cover with R.C.C. Slab, including, providing & fixing of plug for watering, complete with all accessories and fasteners and as per drawing & specifications. | 2 | Job |  | 0
3. | Providing, fixing and connecting of 200 x 200 x 5 mm thick copper earth terminal blocks. | 2 | Job |  | 0
4. | Providing and fixing of Hard Drawn Bare copper wire 2.5mm² (14 SWG) as Earth Continuity Conductor (ECC) with any given mains or sub-mains in all system of wiring including metallic electrical accessories. ( Approx length). | 13000 | Rft. |  | 0
| TOTAL COST OF SECTION "D" |  | (Rs.) |  | 0
S.No. | ITEM DESCRIPTION | QTY. | UNIT | UNIT RATE (Rs) | TOTAL AMOUNT (Rs)
Section "E" Telephone & T.V. System
1. | Providing, installing and connecting of one pin telephone socket outlet with back box recessed on wall complete with all accessories. | 8 | Nos. |  | 0
2. | Same as Item # 1 above but TV Socket outlet | 3 | Nos. |  | 0
3. | Providing & wiring of telephone outlets with 1-3 pair telephone wire in 25mm dia, rigid PVC conduit concealed in R.C.C. or masonary as required, complete in all respects with all accessories. | 7 | Nos. |  | 0
4. | Same as Item # 3 above but Coaxial Cable for TV point | 3 | Nos. |  | 0
5. | Providing, installing and connecting and testing of the following size approved telephone junction box up of 18 SWG sheet steel, with hinged door cover with locking arrangement, with inner lining of 12mm thick teak wood. Complete in all respects .
| a) 10 pair TJB on Ground Floor. | 1 | No. |  | 0
6. | Providing, installing and connecting of following multi-core, telephone cable in 25mm dia in rigid PVC conduit / G.I. pipe concealed in R.C.C. or masonary or buried in ground as per required, complete in all respects with all accessories.
| a) 10 pair Multicore cable | 100 | Rft. |  | 0
| TOTAL COST OF SECTION "E" |  | (Rs.) |  | 0
Contractor
Project Director
CO
Section "A" Internal Electrification
Section "E" Telephone & T.V. System
Section "D" Earthing
Section "B" Light Fittings & Fixtures

## Summary of Internal Elect.
SUMMARY OF COST ESTIMATE FOR
INTERNAL ELECTRICAL WORKS OF
GIRLS HOSTEL
SINDH COLLEGE OF ART AND DESIGN SUKKUR
S.No. | Section | Description |  | Amount (Rs.)
1. | A | Internal Electrification | Rs. | 0
2. | B | Light fittings and Fixtures | Rs. | 0
3. | C | Distribution Boards & Feeders | Rs. | 0
4. | D | Earthing | Rs. | 0
5. | E | Telephone & TV System | Rs. | 0
Total Cost |  |  | Rs.
Contractor
Project Director

## External Electrification
COST ESTIMATE FOR
EXTERNAL ELECTRICAL WORKS OF
GIRLS HOSTEL
SINDH COLLEGE OF ART AND DESIGN SUKKUR
S.No. | ITEM DESCRIPTION | QTY. | UNIT | UNIT RATE (Rs) | TOTAL AMOUNT (Rs)
1. | Providing, laying & connecting of 240mmsq., 3.5 Core, PVC/SWA/PVC from Substation-7 to SMPB laid in ground in RCC pipe including digging of earth and making CC Man-holes with covers at required distance for pulling of cables. Job also involves refilling of Earth and providing cable markers for route of LT cable as per specifications. | 300 | Rft. |  | 0
2. | DB- EXTERNAL
| 10mm², 4Core, PVC/PVC + 6mm² ECC in 38mm dia rigid PVC conduit in ground / floor as required from MDB. | 35 | Rft. |  | 0
TOTAL COST OF SECTION "D" |  |  | (Rs.) |  | 0
Contractor
Project Director
Section "A" Main Feeders & Cables

## Summary of External Elect.
SUMMARY OF COST ESTIMATE FOR
EXTERNAL ELECTRICAL WORKS OF
GIRLS HOSTEL
SINDH COLLEGE OF ART AND DESIGN SUKKUR
S.No. | Section | Description |  | Amount (Rs.)
1 | A | Main Feeder | Rs.
TOTAL COST
Contractor
Project Director