## Schedule
BILL OF QUANTITIES
Discription and Rate of Items based on Composite Schedule of Rates
NAME OF WORK :- ESTABLISHMENT OF WOMEN DEVELOPMENT COMPLEX AT SUKKUR (EXTERNAL ELECTRIFICATION)
Item No. | Quantities | Description of item to be executed at site | Rate | Units | Amount
PART "A" SCHEDULE ITEMS
1 | 22 | Providing & fixing of MS tabular pole as following specification to be fixed on pre-cast foundation with the help of hydraulic crane & manual labour 20ft-(6`` dia) × 5.5ft (5`` dia) × 5.5ft (4`` dia) = 31ft wall thickness 8 SWG Base plate 18`` × 18`` × ¾ `` Hole 4 no’s stiffeners 4 nos. 9 ½``× 4 ½`` × ½`` Making window in the pole required size with LN key provision Two coats red oxide (2 coat) as rust preventive & Of required oil paint (2 coat) as per site requirement & instruction of EI (S.I.No:132 P- No:16) | 36697 | P.No | 807334
2 | 22 | Construction of RCC foundation as per following specification & instruction of EI for 31ft/40ft long tubular pole Excavation of soft/hard soil 3`×3`×5.5` Stone soiling 3`×3`×6`` making lean in the ratio of 1:4:8 Length of MS bolts 6 ½`( ¾ `` dia) 4 no’s & making thread on MS rod Template 16``×16``× ¼`` Rings ¼`` dia round bar 4 no’s to the welded with MS rod RCC foundation ratio 1:2:4 with appropriate size 2`×2`×6.5` (S.I.No:132 P- No:16) | 15168 | P.No | 333696
3 | 44 | 160. Providing & Fixing of street light 250 watts (HPMV) having IP54 classification with 250w lamp, choke, capacitor & Internal wiring complete in all respect at the height up to 31ft as per site requirement and instruction of EI. Make of the above light is as follow | 8455 | P.No | 372020
4 | 1 | Providing & fixing circuit breaker 15,20,30, 40,50,60,75 & 100amp TP (XS-100NS) on prepared board as required (S.I.No:202 P- No:30) | 9261 | P.No | 9261
5 | 440 | Providing & laying (MAIN or SUB MAIN) PVC insulated with size 2-7/.036 copper conductor in ¾’’ dia PVC conduit recessed in the wall or column as required. (S.I.No:11 P- No:2) | 252 | per Meter | 110880
|  |  | TOTAL :- |  | 1633191
PART "B" OLD SCHEDULE ITEMS
1 | 4 | P/F distribution metal board double shutter to accommodate circuit breakers including painting with enemel paint and for other simmilar job on surface (S.I.No:18 P- No:13) | 1426.33 | P.Sft | 5705.32
2 | 110 | P/F Shackle "D" iron belts make of galavanized mild steel flat 1.1/4 x 3 /816" size having a bolt with nut 3" x 3/8" size of clamp 1. 3/4" w 21/2" (CSI No. G 1 P-27). | 118.25 | Each | 13007.5
3 | 110 | P/F galavanized iron bolts for pressures pic insulator (S.I No. B 1 P-27). | 286 | Each | 31460
4 | 110 | P/F 21" channel shackle insulator medium pressure | 47.3 | Each | 5203
5 | 25 | P/F stay with 7/10 G.I wire complete stay rod galvanized thimble sky insulator stay swirel and clamps etc as required (S.I.No: 2(g) P- No:28) | 2295 | P.Point | 57375
6 | 22 | P/F earthing set with 2x2x1/4" cooper plate burried in groud at a depth of 12" or less if water comes out from the ground level with salt and chorcoal ,etc,in/c.making the pit 12"deep by excavation of all type of soil. Earth plat to be connected with No:8 | 3610.04 | Each | 79420.88
|  |  | TOTAL :- |  | 192171.7
Amount Total (CSR)
Part "A" |  | % Above / Below ____________ | Total Amount
Part "B" |  | % Above / Below ____________ | Total Amount
Total "A+B"
NON SCHEDULE ITEMS
1 | 9000 | Supply & erection of alluminium, conductor waist size all size of poles |  | P.Rft
TOTAL :-
| Cost of Bid |  |  | Amount | Position
1. (A) Cost Based on Composite Schedule of Rates
2. (B) Cost Based on Non/Offered Schedule of Rates
TOTAL COST OF BID (C) = TOTAL (A) + TOTAL (B)
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PROVINCIAL BUILDINGS DIVISION
SUKKUR

## Schedule (2)
BILL OF QUANTITIES
Discription and Rate of Items based on Market (Offered Rates)
NAME OF WORK :- UP-GRADATION OF PRIMARY SCHOOL TO MIDDLE SCHOOL IN SUKKUR DISTRICT 2013-14 PROGRAMME AT GBPS KAMIL MAGSI TALUKA SALEH PAT.
Item No. | Quantities | Description of item to be executed at site | Rate | Units | Amount
1 | 132 | P/F gutka brick facing 2 1/4" x 9" x 1 1/2" size and approved shape cement sand mortor including filling with the joints with white slurry using colour pigment matelling i/c leveling smooth finishing curring and sky folding welding etc complete as per specification at as directed by the Engineer Incharge. |  | P.Sft
2 | 1 | P/F piston pump set 1 H.P single phase 220 valts with 1/1/4" x 1/1/4" suction and delivery (Local made ) (Electric) |  | Each
TOTAL :-
Total (b) in words & figures
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
EDUCATION WORKS DIVISION
SUKKUR