## Schedule B
"SCHEDULE "B" ."
NAME OF WOFK:- CONSTRUCTION OF SPECIAL COURT (10) NOS AT CENTRAL PRISON KARACHI (REVISED 20 Nos COURTS (G+1) 10 Nos ON EACH FLOOR AT PRISON KARACHI (ELECTRIFICATION OF REMAINING 10 NOS COURTS(G+1 FLOOR.)
S.NO | Description of item | Quantity |  | Rate | Unit | Amount
1 | LIGHTING FIXTURES
1.1 | Supply installation and connection of the Following lighting fixture as specified in the Legend complete with lamps starters holders Capacitors ballasts etc including all mounting accessories
a | Fixture type A ( surface ) | 130 | Nos |  | EACH
Philips TCS 236 with 2x36 W TLD lamps electronic Blast and M2 reflector
b | Fixture type B ( surface) Ft LED smart surface down light with 1x 12 W LED | 250 | Nos |  | EACH
c | Fixture type C ( surface)Philips TMS 128 with 1x28 W T5 lamp including electronic blast | 50 | Nos |  | EACH
1’2 | Supply installation and connection of 18” dia bracket fan complete with all mounting accessories’ | 20 | Nos |  | Each
3.1 | Supply installation and connection of 56” sweep fan in plastic body including louver complete with all mounting accessories. | 120 | Nos |  | Each
4.1 | Supply installation and connection of 8” dia exhaust fan in plastic body including louver complete with all mounting accessories | 20 | Nos |  | Each
TOTAL
2 | LIGHT / FAN /SOCKET WIRING
2.1 | Providing and installing of light point wring with 3x1.5 Sqmm single core PVC insulated 300/500V grade copper wires in 20mm dia PVC conduit surface/concealed mounted including all accessories connector / junction boxes 1.5 Sq mm 3-core PBVC/PVC cable in flexible PVC conduit for final connection complete in all respect
a) | Light point controlled by one switch | 350 | Nos |  | Each
b) | Light point from point to point | 60 | Nos |  | Each
c) | Ceiling fan point including fan hook box | 120 | Nos |  | Each
d) | Exhaust fan point | 20 | Nos |  | Each
e) | Bracket fan [point | 20 | Nos |  | Each
f) | Circuit wiring from distribution board to switch/ lighting points with 3x2.5 Sqmm single core PVC insulated copper wires in 25mm dia PVC conduit concealed/ surface mounted with all accessories’ | 100 | Nos |  | Each
2.2 | Providing & installing of wiring from distribution board for 13A international switch socket outlets with 3x1-c2.5 sqmm PVC insulated copper wires in 25mm dia pvc conduit canceled/ surface mounted with all accessories | 60 | Nos |  | Each
2.2 a | Same as item 2.2 but wiring point to point . | 140 | Nos |  | Each
2.3 | Providing & installing of wiring for A.C unit from DB to respective load break switch & from load break switch to condensing unit with 3x6 Sq mm single core PVC Insulated copper wires in PVC conduit complete with all accessories including terminations. | 70 | Nos |  | Each
2.4 | Supply and installation of sheet steel back boxes for switches and sockets including complete earth terminals complete with all mounting accessories. | 1200 | Nos |  | Each
2.5 | Supply and installation of following Clipsal E- series switches.
a) | One Gang switch | 30 | Nos |  | Each
b) | Two Gang switch | 80 | Nos |  | Each
c) | Three Gang switch | 40 | Nos |  | Each
d) | Four Gang switch | 50 | Nos |  | Each
e) | Fan Dimmer | 120 | Nos |  | Each
f) | 13Amp international switch socket outlet valance series | 240 | Nos |  | Each
TOTAL
3 | L V SWITCHGEAR
3.1 | Supply installation and connection of the following mixed capacity MCB distribution boards complete with all mounting accessories as per drawings
a | MDB | 1 | NO |  | Each
b | SMDG | 1 | NO |  | Each
c | DB-G1 | 1 | NO |  | Each
d | DB-G-2 | 1 | NO |  | Each
e | DB=G3 | 1 | NO |  | Each
f | DB-G-4 G | 1 | NO |  | Each
g | DB-G-5 G | 1 | NO |  | Each
H | DB-F1 | 1 | NO |  | Each
I | DB-F-2 | 1 | NO |  | Each
J | DB-F-3 | 1 | NO |  | Each
K | DB=F 4 | 1 | NO |  | Each
L | DB-F5 | 1 | NO |  | Each
3.2 | Supply installation and connection of the Following load break switches/MCB suitable for AC3 operation in weather proof steel enclosures with natural and earth terminal complete with all minting accessories
a | 15A DP 10KMCB | 50 | Nos |  | Each
b | 20A DP10KA MCB | 20 | Nos |  | Each
TOTAL
4 | MAIN /SUB MAIN CABLES AND EARTHING
4.1 | Supply installation and connection of the following sub main 600/100V grade PVC insulated stranded / multi core copper cables in already installed cable tray/ conduit complete with all accessories.
(a) | Supply from K ELECTRIC to MDB G F 4-c 240sq mm PVC /pvc cable including excavation and back filling (if REQ) | 65 | Mtr |  | P.Mtr
(b) | From MDB to SMDB 4c-150sqmm PVC/PVC+1x1C70SqmmPVCcables | 40 | Mtr |  | P.Mtr
© | FROM MDB TO DB-GI 4-c 16sqmm PVC/PVC+1x1c=16sqmmPVC cables | 18 | Mtr |  | P.Mtr
(d) | FROM MDB TO DB-G2 4C-16 sqmm pvc/pvc+1XC-16mm PVC cables | 36 | Mtr |  | P.Mtr
(e) | FROM MDB TO DB-G 34-c 16sqmm PVC/PVC +x1c 16sqmm PVC cables | 42 | Mtr |  | P.Mtr
(f) | FROM MDB TO DB G4 4c16sqmm PVC/PVC+1c-16sqmm PVC cables | 52 | Mtr |  | P.Mtr
(g) | FROM MDB TO DB G 5 4c-16cmm pvc 3.0x1c-16sqmm pvc cables | 66 | Mtr |  | P.Mtr
h | From SMDB to DB-FF 1 4c-16sq mm PVC /PVC +1x1c-16 sq mm pvc cables | 18 | Mtr |  | P.Mtr
I | From SMDB to DB-F.F2 4c-16sq mm PVC /PVC +1x1c-16 sq mm pvc cables | 36 | Mtr |  | P.Mtr
J | From SMDB to DB-FF3 4c-16sq mm PVC /PVC +1x1c-16 sq mm pvc cables | 42 | Mtr |  | P.Mtr
k | From SMDB to DB-FF4 4c-16sq mm PVC /PVC +1x1c-16 sq mm pvc cables | 52 | Mtr |  | P.Mtr
m | From SMDB to DB-F F 5 4c-16sq mm PVC /PVC +1x1c-16 sq mm pvc cables | 66 | Mtr |  | P.Mtr
4.2 | Supply and installation of earthling pits complete with copper earth electrode of 1”dia ft long/ green earth (as per req: clamps G/I pipe and all accessories each earth pit is to be provided with a concrete manhole 12x12 x18 deep with heavy duty C.I cover including test clamp complete in all respect/ | 2 | Nos |  | Each
4.3 | Supply installation & connection of following size pvc insulated earthling copper conductor in pvc pipe schedule “D” of req: size from earth pit to MDB
a) | 2x1c-70sq.mm pvc Cable | 30 | Mtr |  | PMtr
(b) | 2x1c-35 sqmm pvc cables | 30 | Mtr |  | PMtr
TOTAL
5 | CABLE TRAY /TRUNKING/G.I. PULL BOXES/PVC PIPS
5.1 | Supply and installation of 14 SWG galvanized sheet steel under floor pull boxes including cover, brass earth terminal, metal cable separators and oil fixing accessories of the following size.
a | 200mmx200mmx50mm | 15 | Nos |  | Each
5.2 | Supplying and installation of 16 SWG floor outlet box with hinged cover suitable for 3Nos international switch socket outlet land l1No l Duplex outlet for data/ voice complete all respect//. | 50 | Nos |  | Each
5.3 | Providing land installation of PVC pipes including all accessories l(e.g bends sockets etc) of the following sizes
a | 100 mm dia PVC pipes for circuit wring | 100 | Mtr |  | PMtr
b. | 50mm dia PVC for circuit wiring | 350 | Mtr |  | PMtr
c. | 32mm dia pvc pipes for circuit wiring | 60 | Mtr |  | PMtr
d | 25mm dia pvc pipe for light wiring | 400 | Mtr |  | Pmtr
TOTAL
6 | WIRING FOR CLOSED CIRCUITIVE SYSTEM
6.1 | Supply installation and connection of RG-6 coaxial cable in 25mm dia pvc conduit from patch panel to cameras complete with all mounting accessories | 1800 | Mtr |  | PMtr
6.2 | Supply installation and connection 3C- 1.5mm2 pvc /pvc cable for power supply to CCTV cameras in PVC conduit | 34 | Nos |  | Each
TOTAL
7 | WIRING FOR FIRE ALARM SYSTEM
7.1 | Supply and installation of addressable type-1 loop fire alarm control panel FACP) | 1 | No |  | Each
7.2 | Supply and installation of addressable type smoke detector | 130 | Nos |  | Each
7.3 | Supply and installation of addressable type manual break glass station | 16 | Nos |  | Each
7.4 | Supply and installation of addressable electric sounder | 18 | Nos |  | Each
7.5 | SUPPLY And installation of wiring of fire alarm system devices with 2c- 1.5 sqmm PVC/PVC in already laid PVC pipe from FACP to devices | 800 | Mtr |  | P.Mtr
7.6 | Testing and commissioning of the entire system by authorized representative of the supplier | 1 | Job |  | job
TOTAL
8 | SOUND SYSTEM
8.1 | Supply & installation of sound system complete with all accessories power supply unit, comprising of the following equipment as per drawing
a | Power amplifier of 120 watt/4 ohms bridge mono with 6 balanced mica inputs through XLR Jacks and 8 line inputs through ¼”jacks complete with2-channel EQ | 1 | No |  | Each
b | Goose neck microphone | 10 | Nos |  | Each
c | Mixer amplifier with 3 mic /line inputs and 3 auxiliary in puts with priority and 120 watts rated outputs | 1 | No |  | Each
d | Surface mount ceiling speaker rated in put 6w 5-25=1-3W) WITH MULTIPLE POWER TAPPING OF 10-5-2.5W0(100v) the speaker shall have a spl of 194db at 1 w/m 1khz and a coverage angle of 180 | 20 | Nos |  | Each
e | Speakers wring with 2c-2,5mm 2 vpc /pvc cable in 25 mm dia Pvc conduit | 82 | Mtr |  | P Mtr
TOTAL
TERMS AND CONDITIONS:-
1. Any typographical error in the Schedule "B" are subject to the correction with the reference to the Schedule of Rates for Electrical works 2012 in force from 12 July 2012 publication No 52/54 as approved by standing rates committee, Sindh Karachi.
2. No. premium shall be paid on Non-Schedule Items.
3. The Contractors quoting exorbitant will be required to submit Rate Analysis to justify their rates within specified time other wise the concerned contractor shall be treated as a quilty of misconduct and he shall be liable to face punitive action under
4. Valid Electrical License from Electerical Inspector Karachi is verified.
| CONTRACTOR. Assistant Engineer |  | Executive Engineer
| Provincial Electrical Sub-Divn-IV, |  | Provincial Building Division-III,
| Karachi. |  | Karachi.