BILL OF QUANTITY

Sr # 61

Name of work: -	Rehabilitation of Water Supply Scheme Mirzapur & Manjhi Khan Chandio Taluka Warah

Head of A/C: -	Production Bonus Programme 2016-17

| Qty: | S.No. | Item of work | Rate | Unit | Amount |
| --- | --- | --- | --- | --- | --- |

A: - A.C TURBINE PUMPING SET  25 BHP

01.providing  & installing in position i/c transportation to site of work Mirzapur Vertical Turbine  Electric Pumping set consisting of Hallow Shaft Electric Vertical Motor SEIMENS Made of 25 BHP 1450 RPM 4 cores of squirrel cage totally enclosed for Doed type Suitable for tropical  limit . The Motor is foot mounted single shaft suitable three phase 50 cycles 380 volts A.C Electric  volts A.C electric supply @ 40 C * ambient insulation class B with non reversible ratched coupled with (KSB Vertical  pump Type (B-8 D-40-consisting of Pumps Bowl assembly with discharge case intermediate Bowl all made of Cast iron  with bronze impellers 142 /134 dynamically balanced with Securely fastened to stainless steel pump shaft connected to lime shaft by means of with threaded coupled columns shaft and top shaft made Carbon Steel Surface discharge made of Cast iron with base for mounting pump Bowl assembly is connected to discharge head with 01 set of Copip assembly 10’ in length of 10x3050  mm dia pump capable of discharging 350 gallons GPM at total head of 120 driven by 04 Pole vertical hallow shaft (SEMENS) motor & Pump setting depth 60 ft Pump set to be supplied with Siemens Motor 25 BHP P/4 pole Electric motor & SEMENSE ASD-5B Starter i/c Installation of the Pumping Set   on cement concrete foundation (1:2:4) with M.S nuts bolts of 5/8” to be embedded in C.C foundation i/c providing and fixing on prepared board  SEMENSE MCU 25 BHP Complete wiring for mains with 3-19/2,14,7/0.44 PVC insulated wire 660 volts grade in 50/80 mm (1”) heavy guage steel conduit on surface as required i/c proving & fixing earthing set with 0.6Mx0.6Mx5.3MM(2’x2’x ½) copper plate buried in the ground at depth of 3.7M(12’) or less as per Pak PWD specification and testing for the pumping set against the required head of 72 hours etc complete. (Approved R.A)

Qty: 2 Sets			@ Rs. 2000000/-			P.Set.		Rs.  4000000/-

Total		Rs:  4000000/-

B: - INTER CONNECTION

01.Providing laying and fixing trenches i/c fitting, jointing and testing etc: complete in all respect the high Density polyethylene P.E pipes (HDPE-100) for W/S confirming ISO 4427/DIN 8074/8075 B.S 3580 & PSI 3051 (PHSI-1, P-25)

20.00 Rft	6” dia		@ Rs. 440/-				P.Rft.		Rs. 8800/-

02. Supplying M.S Flanges (PHSMI No:12, P-17)

Qty: 04 Nos:	6” dia		@Rs: 500/89				P.each		Rs:  6011/-

03. C.I Sluice valve heavy pattern test pressure 21 kg/sq, cm or 300 lbs/sq inch. (PHSMI No:1, P-11)

Qty: 01 Nos:	6” dia		@Rs: 9360/-				P.each		Rs:   4290/-

04. PE Elbow 90 . (PHSMI No:C, P-18)

02 No; 				@Rs: 5436/25				P.Cwt		Rs: 10872/-

05. Supplying Reflex Valve heavy pattern test pressure 21 kg/sq, cm or 300 lbs:/sq: inch(PHSMI No:C, P-11)

Qty: 1 Nos:	6” dia		@Rs: 4062/50				P.each		Rs:  4062/-

06. Supplying Flange Adopter.(NS)

6”dia (160 mm) 2x2=4 Nos:	@Rs: 2025/-				P.each		Rs:  8100/-

07. Butt Fusion Joint (PHSMI-H, P-20)

4 Joints 	6” dia		@Rs: 1000/-				P.Joint		Rs:  4000/-

08. Supplying C.I Gibault Joint (PHSMI-H, P-20)

2 No: 		6” dia		@Rs: 1062/50				P.Joint		Rs:  2125/

2 No: 		8” dia		@Rs: 1381/25				P.Joint		Rs:  2763/

09. Supplying PE Reducer  (PHSMI-H, P-20)

02 No; 		8”x6”		@Rs: 1218/75				P.Joint		Rs: 2438/-

10. Jointing C.I/ M.S. flanged pipe and specials flanged ends inside trenches i/c supply rubber packing of required thickness ruts belts with washers and other tools required for jointing and testing the joints to the specified pressure etc complete ( PHSI No.1 Page-33).

4 Joints	4” dia		@Rs: 938/-				P.Joint		Rs:   3752/-

Total		Rs:  48413/-

For 02 Nos:      2 x 48413/-		=		Rs:  96826/-

C: - P.E PIPE RISING MAIN

01. Excavation for pipe line in trenches i/c pits in soft soil i/c trimming and dressing sides to true alignment and shape leveling of beds of trenches to correct level and grade cutting, joints holes & disposal of surplus earth within one chain or as directed by Engineer Incharge i/c providing fence guards light flanges and temporary crossing for non vehicular traffic where ever required lift upto 5’ and lead upto one chain.    (PHSI No:2,P-46)

11600.00 cft			@Rs: 3600/-			P%0cft.		Rs:  41760/-

02. Providing, Laying,  & fixing in trenches i/c fitting . jointing & testing etc complete in all respects  the high Density polyethylene P.E pipes (HDPE-100)for W/S confiriming ISO DIN 8074/8075 B.S 3580& PSI 3051 (PHSI No: 1, P-25) PN-08

8” dia (225 mm O/D)

800.00 Rft			@Rs: 860/-			P.Rft			Rs: 688000/-

6” dia (225 mm O/D)

500.00 Rft			@Rs: 860/-			P.Rft			Rs: 220000/-

4” dia (225 mm O/D)

500.00 Rft			@Rs: 224/-			P.Rft			Rs: 112000/-

03. Supplying C.I Reducers (PHSI No: 11 P-15 )

8”x6”

2 Nos:				@Rs: 1218/75			P.each			Rs:2438/-

High Density Polyethylene Fitting (PE 100)

4. Supplying Elbow 45º (outer dia) (PHSMI No: A, P-18) (PN-10).

i) 8” dia (225 mm O/D)

2 Nos:				@Rs: 3480/-			P.each			Rs: 6960/-

05. Supplying High Density P.E Equal Tee (outer dia) (PHSMI No: D, P-19) (PN-10)

i) 6” dia (225 mm O/D)

2 Nos:				@Rs: 1950/-			P.each			Rs: 3900/-

ii) 4” dia (  mm O/D)

2 Nos:				@Rs: 1675/-			P.each			Rs: 3350/

6. Supplying High Density P.E Un-Equal Tee (outer dia) (PHSMI No: D, P-19) ) (PN-10)

i) 8”x6”x8” dia (200x90x200 mm O/D)

1 Nos:				@Rs: 3687/50			P.each			Rs: 3688/-

ii) 6”x6”x4” dia

1 Nos:				@Rs: 1375/00			P.each			Rs: 1375/-

7. Supplying High Density P.E Elbow 90o (outer dia) (PHSMI No: F, P-19) ) (PN-10)

i) 8” dia (225 mm O/D)

1 Nos:				@Rs: 8363/40			P.each			Rs: 8363/-

ii) 6” dia (160 mm O/D)

1 Nos:				@Rs: 5436/25			P.each			Rs: 5436/-

ii) 4” dia (110 mm O/D)

1 Nos:				@Rs: 1586/15			P.each			Rs: 1586/-

8. Supplying C.I Gibault Joints (PHSI No: 14 P-16 )

(a). 8” dia

20 Nos:				@Rs: 1381/25			P.each			Rs: 27625/-

(a). 6” dia

12 Nos:				@Rs: 1062/50			P.each			Rs: 12750/-

(a). 4” dia

20 Nos:				@Rs: 731/20			P.each			Rs: 14624/-

9. Supplying Adapter. (M.R)

8” dia	(225mm)	5 Nos:	@Rs: 4725/-			P.each			Rs: 23625/-

6” dia	(160mm)	6 Nos:	@Rs: 2025/-			P.each			Rs: 12150/-

4” dia	(110mm)	8 Nos:	@Rs: 1215/-			P.each			Rs: 9720/-

10. Supplying C.I Sluice valve heavy pattern . (PHSMI No: G, P-20)

1 Nos:			8” dia		@Rs: 17940/-			P.each		           Rs: 17940/-

2 Nos:			6” dia		@Rs: 9360/-			P.each		           Rs: 18720/-

2 Nos:			4” dia		@Rs: 5460/-			P.each		           Rs: 10920/-

11. Supplying C.I Tail Piece n . (PHSMI No: G, P-20)

8” dia			5 Nos:		@Rs: 1056/25			P.each			Rs: 5281/-

6” dia			6 Nos:		@Rs: 618/75			P.each			Rs: 3712/-

4” dia			8 Nos:		@Rs: 487/50			P.each			Rs: 3900/-

12. Butt Fusion Joints ( PHSI No. H P-20).

8” dia	(225mm)	5 Nos:		@Rs: 1800/-			P.each			Rs: 9000/-

6” dia	(160mm)	6 Nos:		@Rs: 1000/-			P.each			Rs: 6000/-

4” dia	(110mm)	8 Nos:		@Rs: 600/-			P.each			Rs: 4800/-

13. Jointing C.I/ M.S. flanged pipes and specials flanged ends inside trenches i/c supply rubber packing of required thickness ruts belts with washers and other tools required for jointing and testing the joints to the specified pressure etc complete ( PHSI No.1 P-40).

8” dia			5 Nos:		@Rs: 940/00			P.each			Rs: 4700/-

6” dia			6 Nos:		@Rs: 938/			P.each			Rs: 5628/-

4” dia			8 Nos:		@Rs: 513/-			P.each			Rs: 4104/-

14. Providing chamber 3½’ x2½” (1064x760mm) in side dimension 4½’(1372mm) deep as per approval design for sluice valve 3” to12” with 18”(457 mm) dia inside cost iron cover and frame (wt: 1 cwt: 3 qr:) fixed in R.C.C 1:2:4 slab 4” (102mm) thick (with 5 lbs: steel per cft) 9” (229mm) thick brick masonry walls set in 1:6 cement mortar 6” (152mm) thick cement concrete 1:3:6 in foundation 1”(25mm) thick cement concrete 1:2:4 flooring ½” (12.50mm) thick cement plaster 1:3 to all inside wall surface and top i/c providing and fixing M.S foot rest at every one feet beyond 2½’ depth curing excavation back filling and disposal of surplus earth etc complete. (PHSI No:1,P-40)

05 Nos:				@Rs: 18820/-			P.each.			Rs:    94100/-

15. Refilling the excavated stuff in trenches in 6” thick layers for leveling dressing i/c watering, ramming to full compaction etc complete. (PHSI No:24,P-53)

10440.00 cft			@Rs: 2760/-			P%0cft.		Rs:  28814/-

Rs: 1416999/-

GENERAL ABSTRACT OF COST

Schedule Items	Non Sch: Items	G. Total

01.  Pumping Machinery		Rs: 	-		Rs: 4000000/-		Rs: 4000000/-

02.  Inter Connection			Rs:     96826/-		Rs:	-		Rs:     96826/-

03. P.E Pipe Rising Main		Rs: 1416999/-		Rs:	-		Rs: 1416999/-

Total: -		Rs: 1513825/-		Rs: 4000000/-		Rs: 5513825/-

Amount Total (a)

--------------------% Above / Below on the rates CSR		Amount to be added/ deducted on the

Basis of premium quoted.

Total: (b)

Total (A) = a + b in words & figure:

CONTRACTOR					  EXECUTIVE ENGINEER

Public Health Engg: Division

Kamber Shahdadkot @ Kamber