## Abstract of all
Appendix-D to Bid
BILL OF QUANTITIES
| Name of Work:- | Construction of C.C Drains, Disposal Works, Pumping Machinery & Providing Laying Jointing P.E Pipe Rising Main for Rehabilitation of Urban Drainage Scheme Thull City.
Sr. No. | Name of Scheme | Schedule Items Amount | Non-Schedule Items Amount | Total Amount
1 | Sub-Work No. 1 Construction of Surface Drains | 33589020.7026 | … | 33589020.7026
2 | Sub-Work No. 2 Construction of C.C Block | 3068348.4848 | … | 3068348.4848
3 | Sub-Work No. 3 Construction of Collecting Tank | 3075838.783 | … | 3075838.783
4 | Sub-Work No. 4 Construction of S/Chamber | 311384.5476 | … | 311384.5476
5 | Sub-Work No. 5 Construction of Pump House | 636622.7793 | … | 636622.7793
6 | Sub-Work No. 6 Construction of Compound Wall | 1237145.5492 | … | 1237145.5492
7 | Sub-Work No. 7 Construction of Treatment Work | 1882066.6143 | … | 1882066.6143
8 | Sub-Work No. 8 Pumping Machinery | 1376548.1508 | 12567850 | 13944398.1508
9 | Sub-Work No. 9 P.E Rising Main | 9761117 | 24700 | 9785817
TOTAL |  | 54938092.6117 | 12592550 | 67530642.6117
| CONTRACTOR | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
CONDITIONS
1 | The work will be carried out as per PWD/PHE specification.
2 | No premium will be allowed on non-schedule items.
3 | Any error and omission in the description or item of work then rate shall be governed with the relevant schedule of rates and technically sanctioned estimate.
4 | The contractor shall have to bring the material to the site of work from quarries mentioned in the technically sanctioned estimate.
| CONTRACTOR | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD

## Schedule B NSD
Appendix-D to Bid
BILL OF QUANTITIES
| Name of Work:- | Construction of C.C Drains, Disposal Works, Pumping Machinery & Providing Laying Jointing P.E Pipe Rising Main for Rehabilitation of Urban Drainage Scheme Thull City.
| Head of Account:- | ____________________________________________
Sr. No. | Item of Work | Quantity |  | Rate |  | Unit | Amount
SUB-WORK NO: 1 CONSTRUCTION OF NEW SURFACE DRAINS
1 | Excavation in foundation of building bridges and other structures i/c dig billing dressing refilling around the structures with excavated Earth watering ramming up to 5ft (b) in ordinary soil (G.S.I-18/ P/4) | 155916.405 | Cft | @Rs | 3176.25 | P%o Cft | Rs | 495229.4814
2 | Cement concrete plain i/c placing compacting finishing and curing complete i/c screening and washing of stone aggregate without shuttering. (G.S.I - 5 P/15) A) Ratio 1:4:8 | 29983.604 | Cft | @Rs | 11288.75 | P% Cft | Rs | 3384774.0965
3 | Construction of standard open type drains connuttee block of C.C 1:2:4 cost of situ to the design profiles i/c cost of mould as per drawing i/c supplying floating cost of cement 1/32” thick to expose surface faces finished smooth curing complete as per drawing design. (P.H.S.I No.D, P/58)
| Type-A | 35420 | Rft | @Rs | 94 | P-Rft | Rs | 3329480
| Type-B | 9250 | Cft | @Rs | 174 | P-Rft | Rs | 1609500
| Type-C | 1400 | Cft | @Rs | 309 | P-Rft | Rs | 432600
4 | Pacca brick work in foundation and plinth in cement sand mortar(1:6) (G.S.I No. 4 P/ 19) | 91441.47 | Cft | @Rs | 11948.36 | P% Cft | Rs | 10925756.0249
5 | Cement plaster (1:4) up to 20’height ½”thick (G.S.I-11/ P/51) | 114164.6 | Sft | @Rs | 2283.93 | P% Sft | Rs | 2607439.5488
6 | R.C.C work i/c all labour and material except the cost of steel reinforcement and its labour for bending and binding which will be paid separately. This rate also includes all kinds of forms moulds lifting shuttering curing rendering and finishing the exposed surface i/c screening and washing of shingle (a) R.C work in roof slab members laid in situ or prrecast laid in position complete in a respect. (i) Ratio 1;2;4 90 lbs cement 2 cft sand 4 cft shingle 1/8” to ¼” gauge. (C.S.I-6 P/16) | 20953.47 | Cft | @Rs | 337 | P-Cft | Rs | 7061319.39
7 | Fabrication of mild steel reinforcement for cement concrete i/c cutting bending laying in position making joints and fastening i/c cost of binding wire also includes removal of rust from bars. (G.S.I- 8 P/16) | 748.33 | Cwt | @Rs | 5001.7 | P-Cwt | Rs | 3742922.161
[6 empty] | Total | Rs | 33589020.7026
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD

## Schedule B CC Block
Appendix-D to Bid
BILL OF QUANTITIES
| Name of Work:- | Construction of C.C Drains, Disposal Works, Pumping Machinery & Providing Laying Jointing P.E Pipe Rising Main for Rehabilitation of Urban Drainage Scheme Thull City.
Head of Account:-
Sr. No. | Item of Work | Quantity |  | Rate |  | Unit | Amount
SUB-WORK NO: 2 CONSTRUCTION OF C.C BLOCK
1 | Barrow pit excavation undressed lead upto 100 ft ordinary soil (G.S.I. No. 3 p/ 1) | 40624 | Cft | @Rs | 2117.5 | P%o Cft | Rs | 86021.32
2 | Earth work compaction (Soft ordinary or hard soil lying earth in 6” layers leveling dressing and watering for compaction etc complete.(G.S.I.No. 13 P/ 3) | 40624 | Cft | @Rs | 263 | P%o Cft | Rs | 10684.112
3 | Cement concrete brick or stone ballast 1 ½” to 2” gauged ratio (1:4:8) (CSI No: 4, P-14) | 13406.001 | Cft | @Rs | 9416.28 | P% Cft | Rs | 1262346.591
4 | Cement concrete plain i/c placing compacting finishing and curing complete i/c screening and washing of stone aggregate without shuttering. (G.S.I - 5 P/15) Ratio 1:2:4 | 10156 | Cft | @Rs | 14429.25 | P% Cft | Rs | 1465434.63
5 | Erection and removal of centering for R.C.C or plain C.C works of deodars wood (2nd class) (b) for partal wood (vertical) (G.S.I.No. 19/a, P/17) | 1270 | Sft | @Rs | 3127.41 | P% Sft | Rs | 39718.107
6 | Earth Work from Nearest Canal 2 Miles | 40624 | Cft | @Rs | 502.52 | P% Cft | Rs | 204143.7248
[6 empty] | Total | Rs | 3068348.4848
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD

## Schedule B CT
Appendix-D to Bid
BILL OF QUANTITIES
| Name of Work:- | Construction of C.C Drains, Disposal Works, Pumping Machinery & Providing Laying Jointing P.E Pipe Rising Main for Rehabilitation of Urban Drainage Scheme Thull City.
| Head of Account:- | PROVINCIAL ADP 2016-17
Sr. No. | Item of Work | Quantity |  | Rate |  | Unit | Amount
SUB-WORK NO: 3 CONSTRUCTION OF COLLECTING TANK
1 | Excavation of well in dry upto 20’ ft height around level and disposal of soil within one chain. (in ordinary soil) (GSI No: 1, P-85) | 6601.85 | Cft | @Rs | 2247.58 | P%o Cft | Rs | 14838.186
2 | R.C.C work i/c all labour and material except the cost of steel reinforcement and its labour for bending and binding which will be paid separately. This rate also includes all kinds of forms moulds lifting shuttering curing rendering and finishing the exposed surface i/c screening and washing of shingle (a) R.C work in roof slab members laid in situ or prrecast laid in position complete in a respect. (i) Ratio 1;2;4 90 lbs cement 2 cft sand 4 cft shingle 1/8” to ¼” gauge. (C.S.I-6 P/16) | 3474.28 | Cft | @Rs | 337 | P-Cft | Rs | 1170832.36
3 | Fabrication of mild steel reinforcement for cement concrete i/c cutting bending laying in position making joints and fastening i/c cost of binding wire also includes removal of rust from bars. (G.S.I- 8 P/16) | 150.8801 | Cwt | @Rs | 5001.7 | P-Cwt | Rs | 754656.9962
4 | Wet Sinking of walls for depth below spring level by means of driver i/c all charges for shoring leading & removal excavated material within one chain. (GSI No: 3, P-85)
| a) 0’ – 5’ | 5936.56 | Cft | @Rs | 11763.8 | P%o Cft | Rs | 69836.5045
| b) 5’ – 10’ | 5936.56 | Cft | @Rs | 24200 | P%o Cft | Rs | 143664.752
| c) 10’ – 15’ | 4749.5 | Cft | @Rs | 37230.77 | P%o Cft | Rs | 176827.5421
5 | Cement concrete brick or stone ballast 1 ½” to 2” gauged ratio (1:4:8) (CSI No: 4, P-14) | 2002.67 | Cft | @Rs | 9416.28 | P% Cft | Rs | 188577.0147
6 | Cement concrete plain i/c placing compacting finishing and curing complete i/c screening and washing of stone aggregate without shuttering. (G.S.I - 5 P/15) A) Ratio 1:4:8 | 981.25 | Cft | @Rs | 11288.75 | P% Cft | Rs | 110770.8594
| B) Ratio 1:3:6 | 981.25 | Cft | @Rs | 12595 | P% Cft | Rs | 123588.4375
| C) Ratio 1:2:4 | 981.25 | Cft | @Rs | 14429.25 | P% Cft | Rs | 141587.0156
7 | Providing "Construction Joints" in concerte work of 9" (225 mm) wide corrugrated PVC Water Stop (with bulb) i/c soldering cost of material and labour. (PHSI No. , P.No. ) | 489.84 | Rft | @Rs | 86 | P-Rft | Rs | 42126.24
8 | Bailing or pumping out sub-soil water during excavation, concreting, cost in Situ concrete or masonary work in foundation etc. (PHSI No.18, P.No.75) | 25512.5 | Cft | @Rs | 543 | P% Cft | Rs | 138532.875
[6 empty] | Total | Rs | 3075838.783
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD

## Schedule B SC
Appendix-D to Bid
BILL OF QUANTITIES
| Name of Work:- | Construction of C.C Drains, Disposal Works, Pumping Machinery & Providing Laying Jointing P.E Pipe Rising Main for Rehabilitation of Urban Drainage Scheme Thull City.
| Head of Account:- | PROVINCIAL ADP 2016-17
Sr. No. | Item of Work | Quantity |  | Rate |  | Unit | Amount
SUB-WORK NO: 4 CONSTRUCTION OF SCREENING CHAMBER
1 | Excavation in foundation of building bridges and other structures i/c dig billing dressing refilling around the structures with excavated Earth watering ramming up to 5ft (b) in ordinary soil (C.S.I-18/ P/5) | 1299.37 | Cft | @Rs | 3176.25 | P%o Cft | Rs | 4127.124
2 | Extra for wet earth work (GSI No.15, P.3) | 669.37 | Cft | @Rs | 1058.75 | P%o Cft | Rs | 708.6955
3 | R.C.C work i/c all labour and material except the cost of steel reinforcement and its labour for bending and binding which will be paid separately. This rate also includes all kinds of forms moulds lifting shuttering curing rendering and finishing the exposed surface i/c screening and washing of shingle (a) R.C work in roof slab members laid in situ or prrecast laid in position complete in a respect. (i) Ratio 1;2;4 90 lbs cement 2 cft sand 4 cft shingle 1/8” to ¼” gauge. (C.S.I-6 P/16) | 464.0103 | Cft | @Rs | 337 | P-Cft | Rs | 156371.4711
4 | Fabrication of mild steel reinforcement for cement concrete i/c cutting bending laying in position making joints and fastening i/c cost of binding wire also includes removal of rust from bars. (G.S.I- 8 P/16) | 18.64 | Cwt | @Rs | 5001.7 | P-Cwt | Rs | 93231.688
5 | Cement concrete brick or stone ballast 1 ½” to 2” gauged ratio (1:4:8) (CSI No: 4, P-14) | 92.63 | Cft | @Rs | 9416.25 | P% Cft | Rs | 8722.2724
6 | Small iron work such as gusset plate liness lenab, girding tank etc including cutting riveting handling erection in position. (CSI No:19, P-91) | 2.96 | Cwt | @Rs | 6420.61 | P-Cwt | Rs | 19005.0056
7 | Errection & Fitting in Position of iron trusses staging of water tanks etc. (CSI No: 3, P-70) | 2.96 | Cwt | @Rs | 271.04 | P-Cwt | Rs | 802.2784
8 | Providing C.I Manhole Cover & Frame i/c Cost of Material etc. (PHSI No: 1, P-35) | 2 | Cwt | @Rs | 6985 | P-Cwt | Rs | 13970
9 | Excavation for pipe lines in trenches and pits in soft soil clay or mud i/c trimming and dressing sides to true alignment and shape leveling of beds of trenches to correct level and grade, cutting joint holes and disposal or surplus earth within a one chain as directed by Engineering incharge, providing fence guards, lights, flags, and temporary crossing for non vehicular traffic where ever required lift upto 5 ft (1.52m) and upto one chain (30.50m) (PHSI No: 1, P-60) Soft Soil | 256 | Cft | @Rs | 3600 | P%o Cft | Rs | 921.6
| Wet Soil | 112 | Cft | @Rs | 5400 | P%o Cft | Rs | 604.8
10 | Providing R.C.C Pipes of ASTM C-76-62 C-76-70 class – II wall bend fixing in trenches i/c cutting fitting and jointing with rubber ring i/c testing with water to specified pressure. (PHSI No: 1, P-22) 18" Dia | 16 | Rft | @Rs | 618 | P-Rft | Rs | 9888
11 | Refilling the excavated stuff in trenches 6” thick layers i/c watering ramming to full compaction etc complete. | 1098.4104 | Cft | @Rs | 2760 | P%o Cft | Rs | 3031.6127
[6 empty] | Total | Rs | 311384.5476
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD

## Schedule B PH
Appendix-D to Bid
BILL OF QUANTITIES
| Name of Work:- | Construction of C.C Drains, Disposal Works, Pumping Machinery & Providing Laying Jointing P.E Pipe Rising Main for Rehabilitation of Urban Drainage Scheme Thull City.
| Head of Account:- | PROVINCIAL ADP 2016-17
Sr. No. | Item of Work | Quantity |  | Rate |  | Unit | Amount
SUB-WORK NO: 5 CONSTRUCTION OF PUMP HOUSE
1 | Excavation in foundation of building bridges and other structures i/c dig billing dressing refilling around the structures with excavated Earth watering ramming up to 5ft (b) in ordinary soil (G.S.I-18/ P/4) | 259.5 | Cft | @Rs | 3176.25 | P%o Cft | Rs | 824.2369
2 | Cement concrete brick or stone ballast 1 ½” to 2” gauged ratio (1:4:8) (CSI No: 4, P-14) | 138.1604 | Cft | @Rs | 9416.25 | P% Cft | Rs | 13009.5287
3 | Pacca brick work in foundation and plinth in cement sand mortar(1:6) (G.S.I No. 4 P/ 19) | 402.57 | Cft | @Rs | 11948.36 | P% Cft | Rs | 48100.5129
4 | Damp proof course with (cement sand and shingle) concrete 1:2:4 i/c two coats of asphalt mixture. (CSI No: 27, P-23) | 71.19 | Cft | @Rs | 3912.85 | P% Cft | Rs | 2785.5579
5 | Filling Watering and Ramming Earth in floor with surplus earth excavated from out side lead upto 1 chain and lift upto 5'. (GSI No: 28, P-18) | 581.47 | Cft | @Rs | 1512.5 | P%o Cft | Rs | 879.4734
6 | Pacca brick work in ground floor in cement sand mortor (1:6) (CSI No.5, P.No.20) | 434.25 | Cft | @Rs | 12674.36 | P% Cft | Rs | 55038.4083
7 | R.C.C work i/c all labour and material except the cost of steel reinforcement and its labour for bending and binding which will be paid separately. This rate also includes all kinds of forms moulds lifting shuttering curing rendering and finishing the exposed surface i/c screening and washing of shingle (a) R.C work in roof slab members laid in situ or prrecast laid in position complete in a respect. (i) Ratio 1;2;4 90 lbs cement 2 cft sand 4 cft shingle 1/8” to ¼” gauge. (G.S.I-6 P/16) | 160.8 | Cft | @Rs | 337 | P-Cft | Rs | 54189.6
8 | Fabrication of mild steel reinforcement for cement concrete i/c cutting bending laying in position making joints and fastening i/c cost of binding wire also includes removal of rust from bars. (G.S.I- 8 P/16) | 6.4609 | Cwt | @Rs | 5001.7 | P-Cwt | Rs | 32315.4835
9 | Providing Laying 3" thick toping cement concrete Ratio 1:2:4 i/c surface finishing dividing into panel (CSI No.16, P.41) 3" Thick | 216 | Sft | @Rs | 4411.82 | P% Sft | Rs | 9529.5312
10 | Cement plaster 1/2" thick (1:6). (CSI No: , P- ) | 767.91 | Sft | @Rs | 2206.6 | P% Sft | Rs | 16944.7021
11 | Cement plaster 3/8" thick (1:4). (CSI No: , P- ) | 767.91 | Sft | @Rs | 2197.52 | P% Sft | Rs | 16874.9758
12 | Cement pointing struck joints on walls. (CSI No: 11, P-51) Ratio 1:3 | 614 | Sft | @Rs | 1213.58 | P% Sft | Rs | 7451.3812
13 | Fabrication of heavy steel work with angles, tees, flat, iron, round and sheet iron for making trusses, girders, tands etc including cutting, tanks etc including cutting drilling rivetting, handling assembling and fixing but excluding errection in position. (CSI No: 2, P-90) | 4.4106 | Cwt | @Rs | 4928.49 | P-Cwt | Rs | 21737.598
14 | Errection and Fitting in Position of Iron Trusses Stagging of Water Tanks etc. (GSI No. 3, P-91) | 4.41 | Sft | @Rs | 271.04 | P-Sft | Rs | 1195.2864
15 | Supplying & Fixing in position iron / steel grill of 3/4" x 1/4" size flat iron of approved design including painting 3 coats etc complete (weight not to be less than 3.7 Lbs / Sq. Foot of finished grill) (GSI No. , P- ) | 24 | Sft | @Rs | 180.5 | P-Sft | Rs | 4332
16 | Painting new surfaces, preparing of surfaces and painting of doors and windows of any type i/c edges. (GSI No: 5 (c), P-69) 3 Coats | 104 | Sft | @Rs | 2116.41 | P% Sft | Rs | 2201.0664
17 | Primary Coat of Chalk Distemper. (GSI No: 23, P-53) | 1091.912 | Sft | @Rs | 442.75 | P% Sft | Rs | 4834.4404
18 | Distempering two coats. (G.S.I No. 23, P.No. 53) | 1091.912 | Sft | @Rs | 1043.9 | P% Sft | Rs | 11398.4694
19 | Colour Washing two coats. (G.S.I No. 25, P.No. 53) | 1705.912 | Sft | @Rs | 859.9 | P% Sft | Rs | 14669.1373
[6 empty] | Total | Rs | 318311.3896
| 02 Nos: Pump Houses = | 2 | x | 318311.3896 |  | = | Rs | 636622.7793
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD

## Schedule B CW
Appendix-D to Bid
BILL OF QUANTITIES
| Name of Work:- | Construction of C.C Drains, Disposal Works, Pumping Machinery & Providing Laying Jointing P.E Pipe Rising Main for Rehabilitation of Urban Drainage Scheme Thull City.
| Head of Account:- | PROVINCIAL ADP 2016-17
Sr. No. | Item of Work | Quantity |  | Rate |  | Unit | Amount
SUB-WORK NO: 6 CONSTRUCTION OF COMPOUND WALL
1 | Excavation in foundation of building bridges and other structures i/c dig billing dressing refilling around the structures with excavated Earth watering ramming up to 5ft (b) in ordinary soil (G.S.I-18/ P/4) | 1944 | Cft | @Rs | 3176.25 | P%o Cft | Rs | 6174.63
2 | Cement concrete brick or stone ballast 1 ½” to 2” gauged ratio (1:4:8) (CSI No: 4, P-14) | 486 | Cft | @Rs | 9416.25 | P% Cft | Rs | 45762.975
3 | Pacca brick work in foundation and plinth in cement sand mortar(1:6) (G.S.I No. 4 P/ 19) | 2726.1 | Cft | @Rs | 11948.36 | P% Cft | Rs | 325724.242
4 | Damp proof course with (cement sand and shingle) concrete 1:2:4 i/c two coats of asphalt mixture. (CSI No: 27, P-23) | 528.84 | Cft | @Rs | 3912.85 | P% Cft | Rs | 20692.7159
5 | Pacca brick work in other than building including stricking of joints upto 20' height (1:6) (CSI No.7, P.No.21) | 1579.5 | Cft | @Rs | 12346.65 | P% Cft | Rs | 195015.3367
6 | Cement pointing struck joints on walls. (CSI No: 11, P-51) Ratio 1:3 | 2106 | Sft | @Rs | 1213.58 | P% Sft | Rs | 25557.9948
7 | Cement plaster 1/2" thick (1:6). (CSI No: , P- ) | 4605.12 | Sft | @Rs | 2206.6 | P% Sft | Rs | 101616.5779
8 | Cement plaster 1:4 upto 12’ height 3/8" thick. (CSI No: 13, P-52) | 4605.12 | Sft | @Rs | 2197.52 | P% Sft | Rs | 101198.433
9 | R.C.C work i/c all labour and material except the cost of steel reinforcement and its labour for bending and binding which will be paid separately. This rate also includes all kinds of forms moulds lifting shuttering curing rendering and finishing the exposed surface i/c screening and washing of shingle (a) R.C work in roof slab members laid in situ or prrecast laid in position complete in a respect. (i) Ratio 1;2;4 90 lbs cement 2 cft sand 4 cft shingle 1/8” to ¼” gauge. (G.S.I-6 P/16) | 155.25 | Cft | @Rs | 337 | P-Cft | Rs | 52319.25
10 | Fabrication of mild steel reinforcement for cement concrete i/c cutting bending laying in position making joints and fastening i/c cost of binding wire also includes removal of rust from bars. (G.S.I- 8 P/16) | 6.23 | Cwt | @Rs | 5001.7 | P-Cwt | Rs | 31160.591
11 | Fabrication of heavy steel work with angles, tees, flat, iron, round and sheet iron for making trusses, girders, tands etc including cutting, tanks etc including cutting drilling rivetting, handling assembling and fixing but excluding errection in position. (CSI No: 2, P-90) | 16.7101 | Cwt | @Rs | 4928.49 | P-Cwt | Rs | 82355.4129
12 | Preparing the Surface & Painting Work Weather Coat. (G.S.I No. 38, P.No. 56) | 10005.1207 | Sft | @Rs | 1948.1 | P% Sft | Rs | 194909.7564
13 | Colour Washing two coats. (G.S.I No. 25, P.No. 53) | 5400 | Sft | @Rs | 859.9 | P% Sft | Rs | 46434.6
14 | Painting new surfaces, preparing of surfaces and painting of doors and windows of any type i/c edges. (GSI No: 5 (c), P-69) 02 Coats | 552 | Sft | @Rs | 1489.68 | P% Sft | Rs | 8223.0336
[6 empty] | Total | Rs | 1237145.5492
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD

## Schedule B TW
Appendix-D to Bid
BILL OF QUANTITIES
| Name of Work:- | Construction of C.C Drains, Disposal Works, Pumping Machinery & Providing Laying Jointing P.E Pipe Rising Main for Rehabilitation of Urban Drainage Scheme Thull City.
| Head of Account:- | PROVINCIAL ADP 2016-17
Sr. No. | Item of Work | Quantity |  | Rate |  | Unit | Amount
SUB-WORK NO: 7 CONSTRUCIONT OF TREATMENT WORK
1 | Excavation for tanks and reservoirs in soft soil i/c trimming dressing sides to true alignment / section profiles and shape, leveling of beds of tanks to correct level and grade i/c laying of earth in 6” layer for construction of banks and dressing and disposal of surplus excavated earth within one chain as directed by Engineer Incharge i/c providing fence guards, lights, flags wherever required, lift up to 5 feet (1.52M) and lead upto one chain (30.5M). (PHSI No: 15, P-49) | 417381.56 | Cft | @Rs | 3000 | P%o Cft | Rs | 1252144.68
2 | Earth Work Compaction soft ordinary or hard soil laying earth in 6”layers leveling dressing and watering for compaction etc complete. (GSI No: 13/b, P-3) | 426375 | Cft | @Rs | 354 | P%o Cft | Rs | 150936.75
3 | Excavation in foundation of building bridges and other structures i/c dig billing dressing refilling around the structures with excavated Earth watering ramming up to 5ft (b) in ordinary soil (G.S.I-18/ P/4) | 794.81 | Cft | @Rs | 3176.25 | P%o Cft | Rs | 2524.5153
4 | Cement concrete plain i/c placing compacting finishing and curing complete i/c screening and washing of stone aggregate without shuttering. (G.S.I - 5 P/15) A) Ratio 1:4:8 | 88.31 | Cft | @Rs | 11288.75 | P% Cft | Rs | 9969.0951
5 | R.C.C work i/c all labour and material except the cost of steel reinforcement and its labour for bending and binding which will be paid separately. This rate also includes all kinds of forms moulds lifting shuttering curing rendering and finishing the exposed surface i/c screening and washing of shingle (a) R.C work in roof slab members laid in situ or prrecast laid in position complete in a respect. (i) Ratio 1;2;4 90 lbs cement 2 cft sand 4 cft shingle 1/8” to ¼” gauge. (C.S.I-6 P/16) | 526.736 | Cft | @Rs | 337 | P-Cft | Rs | 177510.032
6 | Fabrication of mild steel reinforcement for cement concrete i/c cutting bending laying in position making joints and fastening i/c cost of binding wire also includes removal of rust from bars. (G.S.I- 8 P/16) | 21.1635 | Cwt | @Rs | 5001.7 | P-Cwt | Rs | 105853.478
7 | Excavation for pipe lines in trenches and pits in soft soil clay or mud i/c trimming and dressing sides to true alignment and shape leveling of beds of trenches to correct level and grade, cutting joint holes and disposal or surplus earth within a one chain as directed by Engineering incharge, providing fence guards, lights, flags, and temporary crossing for non vehicular traffic where ever required lift upto 5 ft (1.52m) and upto one chain (30.50m) (PHSI No: 1, P-60) | 4096 | Cft | @Rs | 3600 | P%o Cft | Rs | 14745.6
8 | Providing RCC pipes A.S.T.M C-76-62 T/C 76-70 Class II wall B and fixing in trench i/c cutting, fitting and joint with rubber ring i/c testing with water to specified pressure. (PHSI No: B-1, P-17) | 256 | Rft | @Rs | 618 | P-Rft | Rs | 158208
9 | Refilling the excavated stuff on trenches 6”thick leveling i/c watering raming full compaction etc Complete. (PHSI No.24, P-77) | 3686.4 | Cft | @Rs | 2760 | P%o Cft | Rs | 10174.464
[6 empty] | Total | Rs | 1882066.6143
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD

## Schedule B PM
Appendix-D to Bid
BILL OF QUANTITIES
| Name of Work:- | Construction of C.C Drains, Disposal Works, Pumping Machinery & Providing Laying Jointing P.E Pipe Rising Main for Rehabilitation of Urban Drainage Scheme Thull City.
| Head of Account:- | PROVINCIAL ADP 2016-17
Sr. No. | Item of Work | Quantity |  | Rate |  | Unit | Amount
SUB-WORK NO: 8 PUMPING MACHINERY
ZONE-A
A) | Supplying and installing in position i/c transportation at site of work Electric Pumping set 25 BHP (Simens made) frame size 160-L-4 Pole 1500 RPM totally enclosed fan cooled squirrel cage induction motor 3 phase 400 VAC 5% HZ 2% Suitable for VFD Operation Ambient Temperature 40 C Alritude 1000 m above sea level construction IM B3 (loot mounted) degree of protection IP 65 insulation class F service factor 1.1 coupled with KSB KWPZ non-clogging sullage pump type 150-315 size 6" x 6" mounted of KSB steel frame / coupling with sleeve capable of giving discharge 760 GPM against the required head 45 ft i/c installed on cement concrete foundation Ratio 1:2:4 and M.S nuts & bolts of 5/8" dia to be embedded in cement concrete foundation, supplying and fixing Motor control Unit (MCCB) consists of circuit breaker, magnetic contractor, over load protection, under / over voltage protection phase failure proctection, amp meter with current transformer voltmeter with potential transformer automatic star - delta change over switch controlled power cables, indicating lights and all these components are fixed in a metallic dust and smoke proof box etc complete (Siemens Made) i/c providing and laying (main or sub-main) PVC insulated with size 4-7/0.52 (10mm2) copper conductor in 1-1/2" dia PVC conduct on surface P/F earting set with 2'x'2x1/2" copper plate buried in ground at a depth of 12' or less if water comes out from the ground level without salt and chorcoal etc i/c making the pipe 12' deep by excavation of all type of soil earth plain to be connected with c.c bars copper with own in 1/2" G.I Pipe strength from the erath plate i/c earth work in the ground at depth as per PAK PWD Specification and testing the 72 Hours etc complete. | 2 | Sets | @Rs | 1083000 | P-Set | Rs | 2166000
B) | Supplying and installing Diesel Oil Engine 36 BHP (Golden Made) Model GD-186L-2200 RPM coupled with KSB Non-Clogging Sullage Pump Type-KWPZ-150-315 Size 6" x 6" capable discharging 760 GPM against the head of 45 ft i/c frame, pully for Engine & Pump with belt and installing of Pump Set in C.C Foundation with Nuts and Bolts and Testing of the Pumping Set against the required head at 48 Hours. | 1 | Set | @Rs | 925000 | P-Set | Rs | 925000
SUCTION & DELIVERY
1 | Providing Laying & Fixing in trenches i/c fitting jointing and testing etc complete in all respect the high density polythlene PE Pipe (HDPE-100) for W/S confirming ISO 4427/DIN 8074/8075 B.S 3580 & PSI 3051. (PHSI No. 1, P-25) PN-10
| Suction 6" Dia (180m) | 48 | Rft | @Rs | 685 | P-Rft | Rs | 32880
| Delivery 12" Dia (315 m) | 18 | Rft | @Rs | 1998 | P-Rft | Rs | 35964
2 | Supplying C.I bend with flanged ends with holes i/c turning and facing of flanges for all size (SMI No.8, P-11). Bend 90 | 4.03 | Cwt | @Rs | 6096 | P-Cwt | Rs | 24566.88
3 | C.I Tee with flanged ends with holes i/c turning and facing of flanged all size. (PHS(M)I No.8, P.12) 12" Dia | 2.33 | Cwt | @Rs | 6096 | P-Cwt | Rs | 14203.68
4 | Supplying and installing with M.S Pipe Made out of M.S Sheet 3/16" thick i/c folding to correct shape i/c welding etc completed. 6" Dia | 30 | Rft | @Rs | 749.34 | P-Rft | Rs | 22480.2
5 | Providing and Fixing M.S Flanaged made of M.S Plate having a thickness and total weight as mentioned against each item it includes the cost of making hole facing welding nuts bolts rubber paking white lead fitter cartage etc complete. (PHSI No. 8, P-88) 1/2" Thick M.S Plate
| Suction 6" Dia | 12 | Nos: | @Rs | 1520 | Each | Rs | 18240
| Delivery 12" Dia | 16 | Nos: | @Rs | 2952 | Each | Rs | 47232
6 | C.I tapered flat bottomed or central tapered flanged end with holes i/c turning facing flanged for all sizes. (PHS(M)I No.7, P-11) | 1.2899 | Cwt | @Rs | 6096 | P-Cwt | Rs | 7863.2304
7 | C.I Sluice valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. 16, P-11) 6" Dia | 3 | Nos: | @Rs | 9360 | Each | Rs | 28080
8 | Reflex valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. C, P-11)
| Suction 6" Dia | 6 | Nos: | @Rs | 4062.5 | Each | Rs | 24375
9 | Butt Fusion Joint. (PHS(M)I No. H, P-20)
| 6" Dia | 12 | Joints | @Rs | 1000 | P-Joint | Rs | 12000
| 12" Dia | 16 | Joints | @Rs | 2200 | P-Joint | Rs | 35200
10 | Flange Adapter. (Non-Schedule Item)
| 6" Dia | 16 | Joints | @Rs | 2025 | P-Joint | Rs | 32400
| 12" Dia | 16 | Joints | @Rs | 12150 | P-Joint | Rs | 194400
11 | Jointing C.I / M.S flanged and specials pipes and inside a trenches i/c supplying of the rubber packing of the required thickness nuts bolts and washers etc and other tools required for jointing and testing the joints in the specifics pressure etc complete (CSI No.1 P-35).
| 6" Dia | 16 | Joints | @Rs | 938 | P-Joint | Rs | 15008
| 12" Dia | 25 | Joints | @Rs | 2239 | P-Joint | Rs | 55975
[6 empty] | Total | Rs | 3691867.9904
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
Sr. No. | Name of Work | Schedule Item |  | Non-Schedule Item |  | Total
1 | Pumping Machinery | 374067.9904 |  | 3317800 |  | 3691867.9904
TOTAL |  | 374067.9904 |  | 3317800 |  | 3691867.9904
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
ZONE-B
A) | Supplying and installing in position i/c transportation at site of work Electric Pumping set 20 BHP (Simens made) frame size 160-L-4 Pole 1500 RPM totally enclosed fan cooled squirrel cage induction motor 3 phase 400 VAC 5% HZ 2% Suitable for VFD Operation Ambient Temperature 40 C Alritude 1000 m above sea level construction IM B3 (loot mounted) degree of protection IP 65 insulation class F service factor 1.1 coupled with KSB KWPZ non-clogging sullage pump type 100-250 size 5" x 4" mounted of KSB steel frame / coupling with sleeve capable of giving discharge 550 GPM against the required head 65 ft i/c installed on cement concrete foundation Ratio 1:2:4 and M.S nuts & bolts of 5/8" dia to be embedded in cement concrete foundation, supplying and fixing Motor control Unit (MCCB) consists of circuit breaker, magnetic contractor, over load protection, under / over voltage protection phase failure proctection, amp meter with current transformer voltmeter with potential transformer automatic star - delta change over switch controlled power cables, indicating lights and all these components are fixed in a metallic dust and smoke proof box etc complete (Siemens Made) i/c providing and laying (main or sub-main) PVC insulated with size 4-7/0.52 (10mm2) copper conductor in 1-1/2" dia PVC conduct on surface P/F earting set with 2'x'2x1/2" copper plate buried in ground at a depth of 12' or less if water comes out from the ground level without salt and chorcoal etc i/c making the pipe 12' deep by excavation of all type of soil earth plain to be connected with c.c bars copper with own in 1/2" G.I Pipe strength from the erath plate i/c earth work in the ground at depth as per PAK PWD Specification and testing the 72 Hours etc complete. | 1 | Set | @Rs | 786000 | P-Set | Rs | 786000
B) | Supplying and installing Diesel Oil Engine 32 BHP (Golden Made) Model GD-186L-2200 RPM coupled with KSB Non-Clogging Sullage Pump Type-KWPZ-100-250 Size 5" x 4" capable discharging 550 GPM against the head of 60 ft i/c frame, pully for Engine & Pump with belt and installing of Pump Set in C.C Foundation with Nuts and Bolts and Testing of the Pumping Set against the required head at 48 Hours. | 1 | Set | @Rs | 657000 | P-Set | Rs | 657000
SUCTION & DELIVERY
1 | Providing Laying & Fixing in trenches i/c fitting jointing and testing etc complete in all respect the high density polythlene PE Pipe (HDPE-100) for W/S confirming ISO 4427/DIN 8074/8075 B.S 3580 & PSI 3051. (PHSI No. 1, P-25) PN-10
| Suction 6" Dia (160m) | 32 | Rft | @Rs | 530 | P-Rft | Rs | 16960
| Delivery 10" Dia (250 m) | 18 | Rft | @Rs | 1267 | P-Rft | Rs | 22806
2 | Supplying C.I bend with flanged ends with holes i/c turning and facing of flanges for all size (SMI No.8, P-11). Bend 90 | 3.67 | Cwt | @Rs | 6096 | P-Cwt | Rs | 22372.32
3 | C.I Tee with flanged ends with holes i/c turning and facing of flanged all size. (PHS(M)I No.8, P.12) 10" Dia | 1.55 | Cwt | @Rs | 6096 | P-Cwt | Rs | 9448.8
4 | Supplying and installing with M.S Pipe Made out of M.S Sheet 3/16" thick i/c folding to correct shape i/c welding etc completed. 6" Dia | 20 | Rft | @Rs | 749.34 | P-Rft | Rs | 14986.8
5 | Providing and Fixing M.S Flanaged made of M.S Plate having a thickness and total weight as mentioned against each item it includes the cost of making hole facing welding nuts bolts rubber paking white lead fitter cartage etc complete. (PHSI No. 8, P-88) 1/2" Thick M.S Plate
| Suction 6" Dia | 8 | Nos: | @Rs | 1520 | Each | Rs | 12160
| Delivery 10" Dia | 12 | Nos: | @Rs | 2475 | Each | Rs | 29700
6 | C.I tapered flat bottomed or central tapered flanged end with holes i/c turning facing flanged for all sizes. (PHS(M)I No.7, P-11) | 1.72 | Cwt | @Rs | 6096 | P-Cwt | Rs | 10485.12
7 | C.I Sluice valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. 16, P-11) 6" Dia | 2 | Nos: | @Rs | 9360 | Each | Rs | 18720
8 | Reflex valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. C, P-11)
| Suction 6" Dia | 4 | Nos: | @Rs | 4062.5 | Each | Rs | 16250
9 | Butt Fusion Joint. (PHS(M)I No. H, P-20)
| 6" Dia | 8 | Joints | @Rs | 1000 | P-Joint | Rs | 8000
| 10" Dia | 12 | Joints | @Rs | 1800 | P-Joint | Rs | 21600
10 | Flange Adapter. (Non-Schedule Item)
| 6" Dia | 8 | Joints | @Rs | 2025 | P-Joint | Rs | 16200
| 10" Dia | 12 | Joints | @Rs | 7425 | P-Joint | Rs | 89100
11 | Jointing C.I / M.S flanged and specials pipes and inside a trenches i/c supplying of the rubber packing of the required thickness nuts bolts and washers etc and other tools required for jointing and testing the joints in the specifics pressure etc complete (CSI No.1 P-35).
| 6" Dia | 12 | Joints | @Rs | 938 | P-Joint | Rs | 11256
| 10" Dia | 20 | Joints | @Rs | 1576 | P-Joint | Rs | 31520
[6 empty] | Total | Rs | 1794565.04
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
Sr. No. | Name of Work | Schedule Item |  | Non-Schedule Item |  | Total
1 | Pumping Machinery | 246265.04 |  | 1548300 |  | 1794565.04
TOTAL |  | 246265.04 |  | 1548300 |  | 1794565.04
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
ZONE-C
A) | Supplying and installing in position i/c transportation at site of work Electric Pumping set 30 BHP (Simens made) frame size 160-L-4 Pole 1500 RPM totally enclosed fan cooled squirrel cage induction motor 3 phase 400 VAC 5% HZ 2% Suitable for VFD Operation Ambient Temperature 40 C Alritude 1000 m above sea level construction IM B3 (loot mounted) degree of protection IP 65 insulation class F service factor 1.1 coupled with KSB KWPZ non-clogging sullage pump type 100-400 size 5" x 4" mounted of KSB steel frame / coupling with sleeve capable of giving discharge 800 GPM against the required head 60 ft i/c installed on cement concrete foundation Ratio 1:2:4 and M.S nuts & bolts of 5/8" dia to be embedded in cement concrete foundation, supplying and fixing Motor control Unit (MCCB) consists of circuit breaker, magnetic contractor, over load protection, under / over voltage protection phase failure proctection, amp meter with current transformer voltmeter with potential transformer automatic star - delta change over switch controlled power cables, indicating lights and all these components are fixed in a metallic dust and smoke proof box etc complete (Siemens Made) i/c providing and laying (main or sub-main) PVC insulated with size 4-7/0.52 (10mm2) copper conductor in 1-1/2" dia PVC conduct on surface P/F earting set with 2'x'2x1/2" copper plate buried in ground at a depth of 12' or less if water comes out from the ground level without salt and chorcoal etc i/c making the pipe 12' deep by excavation of all type of soil earth plain to be connected with c.c bars copper with own in 1/2" G.I Pipe strength from the erath plate i/c earth work in the ground at depth as per PAK PWD Specification and testing the 72 Hours etc complete. | 1 | Set | @Rs | 1106000 | P-Set | Rs | 1106000
B) | Supplying and installing Diesel Oil Engine 30 BHP (Golden Made) Model GD-1100 B L-2200 RPM coupled with KSB Non-Clogging Sullage Pump Type-KWPZ-100-250 Size 5" x 4" capable discharging 400 GPM against the head of 60 ft i/c frame, pully for Engine & Pump with belt and installing of Pump Set in C.C Foundation with Nuts and Bolts and Testing of the Pumping Set against the required head at 48 Hours. | 1 | Set | @Rs | 616000 | P-Set | Rs | 616000
SUCTION & DELIVERY
1 | Providing Laying & Fixing in trenches i/c fitting jointing and testing etc complete in all respect the high density polythlene PE Pipe (HDPE-100) for W/S confirming ISO 4427/DIN 8074/8075 B.S 3580 & PSI 3051. (PHSI No. 1, P-25) PN-10
| Suction 6" Dia (160m) | 32 | Rft | @Rs | 530 | P-Rft | Rs | 16960
| Delivery 10" Dia (250 m) | 18 | Rft | @Rs | 1267 | P-Rft | Rs | 22806
2 | Supplying C.I bend with flanged ends with holes i/c turning and facing of flanges for all size (SMI No.8, P-11). Bend 90 | 3.67 | Cwt | @Rs | 6096 | P-Cwt | Rs | 22372.32
3 | C.I Tee with flanged ends with holes i/c turning and facing of flanged all size. (PHS(M)I No.8, P.12) 10" Dia | 1.55 | Cwt | @Rs | 6096 | P-Cwt | Rs | 9448.8
4 | Supplying and installing with M.S Pipe Made out of M.S Sheet 3/16" thick i/c folding to correct shape i/c welding etc completed. 6" Dia | 20 | Rft | @Rs | 749.34 | P-Rft | Rs | 14986.8
5 | Providing and Fixing M.S Flanaged made of M.S Plate having a thickness and total weight as mentioned against each item it includes the cost of making hole facing welding nuts bolts rubber paking white lead fitter cartage etc complete. (PHSI No. 8, P-88) 1/2" Thick M.S Plate
| Suction 6" Dia | 8 | Nos: | @Rs | 1520 | Each | Rs | 12160
| Delivery 10" Dia | 12 | Nos: | @Rs | 2475 | Each | Rs | 29700
6 | C.I tapered flat bottomed or central tapered flanged end with holes i/c turning facing flanged for all sizes. (PHS(M)I No.7, P-11) | 1.72 | Cwt | @Rs | 6096 | P-Cwt | Rs | 10485.12
7 | C.I Sluice valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. 16, P-11) 6" Dia | 2 | Nos: | @Rs | 9360 | Each | Rs | 18720
8 | Reflex valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. C, P-11)
| Suction 6" Dia | 4 | Nos: | @Rs | 4062.5 | Each | Rs | 16250
9 | Butt Fusion Joint. (PHS(M)I No. H, P-20)
| 6" Dia | 8 | Joints | @Rs | 1000 | P-Joint | Rs | 8000
| 10" Dia | 12 | Joints | @Rs | 1800 | P-Joint | Rs | 21600
10 | Flange Adapter. (Non-Schedule Item)
| 6" Dia | 8 | Joints | @Rs | 2025 | P-Joint | Rs | 16200
| 10" Dia | 12 | Joints | @Rs | 7425 | P-Joint | Rs | 89100
11 | Jointing C.I / M.S flanged and specials pipes and inside a trenches i/c supplying of the rubber packing of the required thickness nuts bolts and washers etc and other tools required for jointing and testing the joints in the specifics pressure etc complete (CSI No.1 P-35).
| 6" Dia | 12 | Joints | @Rs | 938 | P-Joint | Rs | 11256
| 10" Dia | 20 | Joints | @Rs | 1576 | P-Joint | Rs | 31520
[6 empty] | Total | Rs | 2073565.04
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
Sr. No. | Name of Work | Schedule Item |  | Non-Schedule Item |  | Total
1 | Pumping Machinery | 246265.04 |  | 1827300 |  | 2073565.04
TOTAL |  | 246265.04 |  | 1827300 |  | 2073565.04
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
ZONE-D
A) | Supplying and installing in position i/c transportation at site of work Electric Pumping set 20 BHP (Simens made) frame size 160-L-4 Pole 1500 RPM totally enclosed fan cooled squirrel cage induction motor 3 phase 400 VAC 5% HZ 2% Suitable for VFD Operation Ambient Temperature 40 C Alritude 1000 m above sea level construction IM B3 (loot mounted) degree of protection IP 65 insulation class F service factor 1.1 coupled with KSB KWPZ non-clogging sullage pump type 65-315 size 3" x 2 1/2" mounted of KSB steel frame / coupling with sleeve capable of giving discharge 415 GPM against the required head 70 ft i/c installed on cement concrete foundation Ratio 1:2:4 and M.S nuts & bolts of 5/8" dia to be embedded in cement concrete foundation, supplying and fixing Motor control Unit (MCCB) consists of circuit breaker, magnetic contractor, over load protection, under / over voltage protection phase failure proctection, amp meter with current transformer voltmeter with potential transformer automatic star - delta change over switch controlled power cables, indicating lights and all these components are fixed in a metallic dust and smoke proof box etc complete (Siemens Made) i/c providing and laying (main or sub-main) PVC insulated with size 4-7/0.52 (10mm2) copper conductor in 1-1/2" dia PVC conduct on surface P/F earting set with 2'x'2x1/2" copper plate buried in ground at a depth of 12' or less if water comes out from the ground level without salt and chorcoal etc i/c making the pipe 12' deep by excavation of all type of soil earth plain to be connected with c.c bars copper with own in 1/2" G.I Pipe strength from the erath plate i/c earth work in the ground at depth as per PAK PWD Specification and testing the 72 Hours etc complete. | 1 | Set | @Rs | 772000 | P-Set | Rs | 772000
B) | Supplying and installing Diesel Oil Engine 30 BHP (Golden Made) Model GD-186L-2200 RPM coupled with KSB Non-Clogging Sullage Pump Type-KWPZ-65-315 Size 3" x 2 1/2" capable discharging 415 GPM against the head of 70 ft i/c frame, pully for Engine & Pump with belt and installing of Pump Set in C.C Foundation with Nuts and Bolts and Testing of the Pumping Set against the required head at 48 Hours. | 1 | Set | @Rs | 632000 | P-Set | Rs | 632000
SUCTION & DELIVERY
1 | Providing Laying & Fixing in trenches i/c fitting jointing and testing etc complete in all respect the high density polythlene PE Pipe (HDPE-100) for W/S confirming ISO 4427/DIN 8074/8075 B.S 3580 & PSI 3051. (PHSI No. 1, P-25) PN-10
| Suction 3" Dia (90m) | 32 | Rft | @Rs | 178 | P-Rft | Rs | 5696
| Delivery 6" Dia (160 m) | 18 | Rft | @Rs | 530 | P-Rft | Rs | 9540
2 | Supplying C.I bend with flanged ends with holes i/c turning and facing of flanges for all size (SMI No.8, P-11). Bend 90 | 1.35 | Cwt | @Rs | 6096 | P-Cwt | Rs | 8229.6
3 | C.I Tee with flanged ends with holes i/c turning and facing of flanged all size. (PHS(M)I No.8, P.12) 6" Dia | 0.46 | Cwt | @Rs | 6096 | P-Cwt | Rs | 2804.16
4 | Supplying and installing with M.S Pipe Made out of M.S Sheet 3/16" thick i/c folding to correct shape i/c welding etc completed. 3" Dia | 20 | Rft | @Rs | 385.89 | P-Rft | Rs | 7717.8
5 | Providing and Fixing M.S Flanaged made of M.S Plate having a thickness and total weight as mentioned against each item it includes the cost of making hole facing welding nuts bolts rubber paking white lead fitter cartage etc complete. (PHSI No. 8, P-88) 1/2" Thick M.S Plate
| Suction 3" Dia | 8 | Nos: | @Rs | 945 | Each | Rs | 7560
| Delivery 6" Dia | 10 | Nos: | @Rs | 1520 | Each | Rs | 15200
6 | C.I tapered flat bottomed or central tapered flanged end with holes i/c turning facing flanged for all sizes. (PHS(M)I No.7, P-11) | 0.51 | Cwt | @Rs | 6096 | P-Cwt | Rs | 3108.96
7 | C.I Sluice valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. 16, P-11) 3" Dia | 2 | Nos: | @Rs | 4290 | Each | Rs | 8580
8 | Reflex valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. C, P-11)
| Suction 3" Dia | 4 | Nos: | @Rs | 1543.75 | Each | Rs | 6175
9 | Butt Fusion Joint. (PHS(M)I No. H, P-20)
| 3" Dia | 8 | Joints | @Rs | 600 | P-Joint | Rs | 4800
| 6" Dia | 10 | Joints | @Rs | 1000 | P-Joint | Rs | 10000
10 | Flange Adapter. (Non-Schedule Item)
| 3" Dia | 8 | Joints | @Rs | 675 | P-Joint | Rs | 5400
| 6" Dia | 10 | Joints | @Rs | 2025 | P-Joint | Rs | 20250
11 | Jointing C.I / M.S flanged and specials pipes and inside a trenches i/c supplying of the rubber packing of the required thickness nuts bolts and washers etc and other tools required for jointing and testing the joints in the specifics pressure etc complete (CSI No.1 P-35).
| 3" Dia | 12 | Joints | @Rs | 499 | P-Joint | Rs | 5988
| 6" Dia | 10 | Joints | @Rs | 938 | P-Joint | Rs | 9380
[6 empty] | Total | Rs | 1534429.52
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
Sr. No. | Name of Work | Schedule Item |  | Non-Schedule Item |  | Total
1 | Pumping Machinery | 104779.52 |  | 1429650 |  | 1534429.52
TOTAL |  | 104779.52 |  | 1429650 |  | 1534429.52
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
ZONE-G
A) | Supplying and installing in position i/c transportation at site of work Electric Pumping set 20 BHP (Simens made) frame size 160-L-4 Pole 1500 RPM totally enclosed fan cooled squirrel cage induction motor 3 phase 400 VAC 5% HZ 2% Suitable for VFD Operation Ambient Temperature 40 C Alritude 1000 m above sea level construction IM B3 (loot mounted) degree of protection IP 65 insulation class F service factor 1.1 coupled with KSB KWPZ non-clogging sullage pump type 100-250 size 5" x 6" mounted of KSB steel frame / coupling with sleeve capable of giving discharge 550 GPM against the required head 60 ft i/c installed on cement concrete foundation Ratio 1:2:4 and M.S nuts & bolts of 5/8" dia to be embedded in cement concrete foundation, supplying and fixing Motor control Unit (MCCB) consists of circuit breaker, magnetic contractor, over load protection, under / over voltage protection phase failure proctection, amp meter with current transformer voltmeter with potential transformer automatic star - delta change over switch controlled power cables, indicating lights and all these components are fixed in a metallic dust and smoke proof box etc complete (Siemens Made) i/c providing and laying (main or sub-main) PVC insulated with size 4-7/0.52 (10mm2) copper conductor in 1-1/2" dia PVC conduct on surface P/F earting set with 2'x'2x1/2" copper plate buried in ground at a depth of 12' or less if water comes out from the ground level without salt and chorcoal etc i/c making the pipe 12' deep by excavation of all type of soil earth plain to be connected with c.c bars copper with own in 1/2" G.I Pipe strength from the erath plate i/c earth work in the ground at depth as per PAK PWD Specification and testing the 72 Hours etc complete. | 2 | Sets | @Rs | 786000 | P-Set | Rs | 1572000
B) | Supplying and installing Diesel Oil Engine 30 BHP (Golden Made) Model GD-1100 B L-2200 RPM coupled with KSB Non-Clogging Sullage Pump Type-KWPZ-100-250 Size 5" x 4" capable discharging 350 GPM against the head of 60 ft i/c frame, pully for Engine & Pump with belt and installing of Pump Set in C.C Foundation with Nuts and Bolts and Testing of the Pumping Set against the required head at 48 Hours. | 1 | Set | @Rs | 644000 | P-Set | Rs | 644000
SUCTION & DELIVERY
1 | Providing Laying & Fixing in trenches i/c fitting jointing and testing etc complete in all respect the high density polythlene PE Pipe (HDPE-100) for W/S confirming ISO 4427/DIN 8074/8075 B.S 3580 & PSI 3051. (PHSI No. 1, P-25) PN-10
| Suction 6" Dia (160m) | 48 | Rft | @Rs | 530 | P-Rft | Rs | 25440
| Delivery 10" Dia (250 m) | 18 | Rft | @Rs | 1267 | P-Rft | Rs | 22806
2 | Supplying C.I bend with flanged ends with holes i/c turning and facing of flanges for all size (SMI No.8, P-11). Bend 90 | 4.0361 | Cwt | @Rs | 6096 | P-Cwt | Rs | 24604.0656
3 | C.I Tee with flanged ends with holes i/c turning and facing of flanged all size. (PHS(M)I No.8, P.12) 10" Dia | 1.5563 | Cwt | @Rs | 6096 | P-Cwt | Rs | 9487.2048
4 | Supplying and installing with M.S Pipe Made out of M.S Sheet 3/16" thick i/c folding to correct shape i/c welding etc completed. 6" Dia | 30 | Rft | @Rs | 749.34 | P-Rft | Rs | 22480.2
5 | Providing and Fixing M.S Flanaged made of M.S Plate having a thickness and total weight as mentioned against each item it includes the cost of making hole facing welding nuts bolts rubber paking white lead fitter cartage etc complete. (PHSI No. 8, P-88) 1/2" Thick M.S Plate
| Suction 6" Dia | 12 | Nos: | @Rs | 1520 | Each | Rs | 18240
| Delivery 10" Dia | 12 | Nos: | @Rs | 2475 | Each | Rs | 29700
6 | C.I tapered flat bottomed or central tapered flanged end with holes i/c turning facing flanged for all sizes. (PHS(M)I No.7, P-11) | 2.5875 | Cwt | @Rs | 6096 | P-Cwt | Rs | 15773.4
7 | C.I Sluice valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. 16, P-11) 4" Dia | 3 | Nos: | @Rs | 5460 | Each | Rs | 16380
8 | Reflex valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. C, P-11)
| Suction 6" Dia | 3 | Nos: | @Rs | 4062.5 | Each | Rs | 12187.5
| Delivery 4" Dia | 3 | Nos: | @Rs | 1706.25 | Each | Rs | 5118.75
9 | Butt Fusion Joint. (PHS(M)I No. H, P-20)
| 6" Dia | 12 | Joints | @Rs | 1000 | P-Joint | Rs | 12000
| 10" Dia | 12 | Joints | @Rs | 1800 | P-Joint | Rs | 21600
10 | Flange Adapter. (Non-Schedule Item)
| 6" Dia | 12 | Joints | @Rs | 2025 | P-Joint | Rs | 24300
| 10" Dia | 12 | Joints | @Rs | 7425 | P-Joint | Rs | 89100
11 | Jointing C.I / M.S flanged and specials pipes and inside a trenches i/c supplying of the rubber packing of the required thickness nuts bolts and washers etc and other tools required for jointing and testing the joints in the specifics pressure etc complete (CSI No.1 P-35).
| 6" Dia | 12 | Joints | @Rs | 938 | P-Joint | Rs | 11256
| 10" Dia | 10 | Joints | @Rs | 1576 | P-Joint | Rs | 15760
| 4" Dia | 6 | Joints | @Rs | 513 | P-Joint | Rs | 3078
[6 empty] | Total | Rs | 2595311.1204
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
Sr. No. | Name of Work | Schedule Item |  | Non-Schedule Item |  | Total
1 | Pumping Machinery | 265911.1204 |  | 2329400 |  | 2595311.1204
TOTAL |  | 265911.1204 |  | 2329400 |  | 2595311.1204
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
ZONE-H
A) | Supplying and installing in position i/c transportation at site of work Electric Pumping set 15 BHP (Simens made) frame size 160-L-4 Pole 1500 RPM totally enclosed fan cooled squirrel cage induction motor 3 phase 400 VAC 5% HZ 2% Suitable for VFD Operation Ambient Temperature 40 C Alritude 1000 m above sea level construction IM B3 (loot mounted) degree of protection IP 65 insulation class F service factor 1.1 coupled with KSB KWPZ non-clogging sullage pump type 65-315 size 3" x 2 x 1/2" mounted of KSB steel frame / coupling with sleeve capable of giving discharge 440 GPM against the required head 50 ft i/c installed on cement concrete foundation Ratio 1:2:4 and M.S nuts & bolts of 5/8" dia to be embedded in cement concrete foundation, supplying and fixing Motor control Unit (MCCB) consists of circuit breaker, magnetic contractor, over load protection, under / over voltage protection phase failure proctection, amp meter with current transformer voltmeter with potential transformer automatic star - delta change over switch controlled power cables, indicating lights and all these components are fixed in a metallic dust and smoke proof box etc complete (Siemens Made) i/c providing and laying (main or sub-main) PVC insulated with size 4-7/0.52 (10mm2) copper conductor in 1-1/2" dia PVC conduct on surface P/F earting set with 2'x'2x1/2" copper plate buried in ground at a depth of 12' or less if water comes out from the ground level without salt and chorcoal etc i/c making the pipe 12' deep by excavation of all type of soil earth plain to be connected with c.c bars copper with own in 1/2" G.I Pipe strength from the erath plate i/c earth work in the ground at depth as per PAK PWD Specification and testing the 72 Hours etc complete. | 2 | Sets | @Rs | 745000 | P-Set | Rs | 1490000
B) | Supplying and installing Diesel Oil Engine 23 BHP (Golden Made) Model GD-1100 B L-2200 RPM coupled with KSB Non-Clogging Sullage Pump Type-KWPZ-65-315 Size 3" x 2 1/2" capable discharging 440 GPM against the head of 50 ft i/c frame, pully for Engine & Pump with belt and installing of Pump Set in C.C Foundation with Nuts and Bolts and Testing of the Pumping Set against the required head at 48 Hours. | 1 | Set | @Rs | 593000 | P-Set | Rs | 593000
SUCTION & DELIVERY
1 | Providing Laying & Fixing in trenches i/c fitting jointing and testing etc complete in all respect the high density polythlene PE Pipe (HDPE-100) for W/S confirming ISO 4427/DIN 8074/8075 B.S 3580 & PSI 3051. (PHSI No. 1, P-25) PN-10
| Suction 3" Dia (90m) | 48 | Rft | @Rs | 178 | P-Rft | Rs | 8544
| Delivery 6" Dia (160 m) | 18 | Rft | @Rs | 530 | P-Rft | Rs | 9540
2 | Supplying C.I bend with flanged ends with holes i/c turning and facing of flanges for all size (SMI No.8, P-11). Bend 90 | 1.49 | Cwt | @Rs | 6096 | P-Cwt | Rs | 9083.04
3 | C.I Tee with flanged ends with holes i/c turning and facing of flanged all size. (PHS(M)I No.8, P.12) 6" Dia | 0.93 | Cwt | @Rs | 6096 | P-Cwt | Rs | 5669.28
4 | Supplying and installing with M.S Pipe Made out of M.S Sheet 3/16" thick i/c folding to correct shape i/c welding etc completed. 3" Dia | 30 | Rft | @Rs | 385.89 | P-Rft | Rs | 11576.7
5 | Providing and Fixing M.S Flanaged made of M.S Plate having a thickness and total weight as mentioned against each item it includes the cost of making hole facing welding nuts bolts rubber paking white lead fitter cartage etc complete. (PHSI No. 8, P-88) 1/2" Thick M.S Plate
| Suction 6" Dia | 12 | Nos: | @Rs | 1520 | Each | Rs | 18240
| Delivery 3" Dia | 12 | Nos: | @Rs | 945 | Each | Rs | 11340
6 | C.I tapered flat bottomed or central tapered flanged end with holes i/c turning facing flanged for all sizes. (PHS(M)I No.7, P-11) | 0.77 | Cwt | @Rs | 6096 | P-Cwt | Rs | 4693.92
7 | C.I Sluice valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. 16, P-11) 3" Dia | 3 | Nos: | @Rs | 4290 | Each | Rs | 12870
8 | Reflex valve heavy pattern test pressure 21 kg / sq, cm or 300 lbs / sq inch. (PHS(M)I No. C, P-11)
| Suction 3" Dia | 6 | Nos: | @Rs | 1543.75 | Each | Rs | 9262.5
9 | Butt Fusion Joint. (PHS(M)I No. H, P-20)
| 6" Dia | 12 | Joints | @Rs | 1000 | P-Joint | Rs | 12000
| 3" Dia | 12 | Joints | @Rs | 600 | P-Joint | Rs | 7200
10 | Flange Adapter. (Non-Schedule Item)
| 6" Dia | 12 | Joints | @Rs | 2025 | P-Joint | Rs | 24300
| 3" Dia | 12 | Joints | @Rs | 675 | P-Joint | Rs | 8100
11 | Jointing C.I / M.S flanged and specials pipes and inside a trenches i/c supplying of the rubber packing of the required thickness nuts bolts and washers etc and other tools required for jointing and testing the joints in the specifics pressure etc complete (CSI No.1 P-35).
| 6" Dia | 12 | Joints | @Rs | 938 | P-Joint | Rs | 11256
| 3" Dia | 16 | Joints | @Rs | 499 | P-Joint | Rs | 7984
[6 empty] | Total | Rs | 2254659.44
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
Sr. No. | Name of Work | Schedule Item |  | Non-Schedule Item |  | Total
1 | Pumping Machinery | 139259.44 |  | 2115400 |  | 2254659.44
TOTAL |  | 139259.44 |  | 2115400 |  | 2254659.44
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
ABSTRACT OF PUMPING MACHINERY
Sr. No. | Name of Work | Schedule Item |  | Non-Schedule Item |  | Total
1 | ZONE-A | 374067.9904 |  | 3317800 |  | 3691867.9904
2 | ZONE-B | 246265.04 |  | 1548300 |  | 1794565.04
3 | ZONE-C | 246265.04 |  | 1827300 |  | 2073565.04
4 | ZONE-D | 104779.52 |  | 1429650 |  | 1534429.52
5 | ZONE-G | 265911.1204 |  | 2329400 |  | 2595311.1204
6 | ZONE-H | 139259.44 |  | 2115400 |  | 2254659.44
TOTAL |  | 1376548.1508 |  | 12567850 |  | 13944398.1508
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD

## Schedule B PE RM
Appendix-D to Bid
BILL OF QUANTITIES
| Name of Work:- | Construction of C.C Drains, Disposal Works, Pumping Machinery & Providing Laying Jointing P.E Pipe Rising Main for Rehabilitation of Urban Drainage Scheme Thull City.
| Head of Account:- | Provincial ADP 2016-17
Sr. No. | Item of Work | Quantity |  | Rate |  | Unit | Amount
SUB-WORK NO: 9 P.E RISING MAIN
1 | Dismentalling for Road Cutting. (CSI No.51, P.No.13) | 13125 | Cft | @Rs | 605 | P% Cft | Rs | 79406.25
2 | Dismentalling Cement concerte reinforced seperating reinforcement from concrete cleaning and straighting the same. (CSI No. 20, P.No.10) | 52.5 | Cft | @Rs | 5445 | P% Cft | Rs | 2858.625
3 | Excavation for pipe lines in trenches and pits in soft soil i/c trimming and dressing sides to true alignment and shape leveling of beds of trenches to correct level and grade cutting joint holes and disposal or surplus earth within a one chain as directed by Engineering incharge providing fence guards. Lights flags and temporary crossing for non vehicular traffic where ever required lift upto 5ft: (1.52m)and lead upto one chain (30.50m) (PHSI No.1, P.No.60) | 83975 | Cft | @Rs | 3600 | P%o Cft | Rs | 302310
4 | Excavation for pipe lines in trenches and pits in Wet soil i/c trimming and dressing sides to true alignment and shape leveling of beds of trenches to correct level and grade cutting joint holes and disposal or surplus earth within a one chain as directed by Engineering incharge providing fence guards. Lights flags and temporary crossing for non vehicular traffic where ever required lift upto 5ft: (1.52m)and lead upto one chain (30.50m) (PHSI No.1, P.No.60) | 500 | Cft | @Rs | 5400 | P%o Cft | Rs | 2700
5 | Providing, Laying & Fixing in trench i/c fitting, jointing & testing etc complete in all repsect the high Density Polythylene PE Pipes (HDPE-100) for W/S confirming ISO 4427/DIN8074/8075 B.S 3580 & PSI 3051. (P-N-08) (PHSI No.1, P.No.25)
| 20" Dia (500 mm) | 250 | Rft | @Rs | 4205 | P-Rft | Rs | 1051250
| 10" Dia (250 mm) | 2700 | Rft | @Rs | 1043 | P-Rft | Rs | 2816100
| 8" Dia (225 mm) | 5900 | Rft | @Rs | 860 | P-Rft | Rs | 5074000
6 | Special cost iron fitting for P.E Pipe.
a) | P.E Elbow 90 Degree (SMI No.1, P.No.18)
| 20" Dia (500 mm) | 1 | No: | @Rs | 33201 | Each | Rs | 33201
| 10" Dia (250 mm) | 2 | Nos: | @Rs | 8469 | Each | Rs | 16938
| 8" Dia (225 mm) | 6 | Nos: | @Rs | 6874 | Each | Rs | 41244
b) | P.E Elbow 45 Degree (SMI No.1, P.No.18)
| 10" Dia (250 mm) | 2 | Nos: | @Rs | 6775 | Each | Rs | 13550
| 8" Dia (225 mm) | 4 | Nos: | @Rs | 5500 | Each | Rs | 22000
c) | P.E Tee Equal. (SMI No. , P.No. )
| 10" Dia (250 mm) | 2 | Nos: | @Rs | 10163 | Each | Rs | 20326
| 8" Dia (225 mm) | 4 | Nos: | @Rs | 8249 | Each | Rs | 32996
d) | Butt Fusion Joint. (SMI No.H, P.No.50)
| 7" to 10" | 20 | Joints | @Rs | 1800 | P-Joint | Rs | 36000
| 20" to 24" | 2 | Joints | @Rs | 3200 | P-Joint | Rs | 6400
e) | P.E Reducer. (NSI)
| 10" to 8" | 2 | Nos: | @Rs | 12350 | Each | Rs | 24700
7 | Refilling the excavated stuff on trenches 6”thick leveling i/c watering raming full compaction etc Complete. (PHSI No.24, P-77) | 76028 | Cft | @Rs | 2760 | P%o Cft | Rs | 209837.28
[6 empty] | Total | Rs | 9785817.155
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD
Sr. No. | Name of Work | Schedule Item |  | Non-Schedule Item |  | Total
1 | P.E.Rising Main | 9761117.155 |  | 24700 |  | 9785817.155
TOTAL |  | 9761117.155 |  | 24700 |  | 9785817.155
| CONTRACTOR |  |  | EXECUTIVE ENGINEER
PUBLIC HEALTH ENGG: DIVISION
JACOBABAD