## R. Civ Stru..
BILL OF QUANTITIES
(A) Description and rate of Items based on Composite Schedule of Rates.
Name of Work |  | REPAIR OF CIVIL STRUCTURE, DISTRIBUTION SYSTEM, PUMPING MACHINERY & SUPPLYING, INSTALLING & TESTING NEW PUMPING MACHINERY 10 BHP (1 SET) FOR RURAL WATER SUPPLY SCHEME QURBAN SHAHEED RIND TALUKA NAWABSHAH
PART-A |  | REPAIR OF CIVIL STURCUTRE
Item No. | Description of item to be executed at site |  |  |  | Unit | Quantity | Rate | Amount in Rupees
1 | Cement, Plaster (1:4) 1/2" thick up to 12’ height (GSI No.13 P-52) |  |  |  | P: % Sft: | 2163 | 2283.93 | 49401.4059
2 | Earth work excavation in ASHES and soft soil or silt clearance undressed lead upto 50' ft: (GSI No. 2 P-1) |  |  |  | P: %0 Cft: | 12960 | 1663.75 | 21562.2
3 | Cement, Pointing struck joint on walls (1:3) (GSI No.19 P-53) |  |  |  | P: % Sft: | 172 | 1213.58 | 2087.3576
4 | R.C.C work in roof slab beams columns rafts lintels and other structural members laid in situ or prrecast laid in position complete in all respect. (I) Ratio 1:2:4 Lbs cement2 Cft, sand 4 cft shingle1/8” to ¼” gauge (GSI No. 6 P-17) |  |  |  | P: Cft: | 224 | 337 | 75488
5 | Fabrication of mild steel reinforcement for C.C i/c cutting, bending, laying in position making joints and fastening i/c cost of binding wire(also i/c removal of rust from bars) (GSI No. 8 P-17) |  |  |  | P: Cwt: | 8 | 5001.7 | 40013.6
6 | Making and fixing steel grated door with 1/16” thick sheeting angle iron frame 2”x2”x 3/8” and ¾” sq: bars 4” Center to center with locking arrangement (GSI No. 24 P-92) |  |  |  | P: Sft: | 72 | 726.72 | 52323.84
7 | Painting new surface preparing surface and painting doors and windows any type i/c edges (GSI No.5 (c) P-70) |  |  |  | P: % Sft: | 415 | 2116.41 | 8783.1015
8 | Providing and laying 2” thick to toping Cement Concrete (1:2:4) I/c surface, finishing and dividing in to panel (GSI No. 16 P-42) |  |  |  | P: % Sft: | 192 | 9416.28 | 18079.2576
9 | Cartage of Earth (Lead 1 Mile) |  |  |  | P: % Cft: | 12960 | 407 | 52747.2
10 | White washing of one coat (GSI No.26 P-54) |  |  |  | P: % Sft: | 2335 | 416.63 | 9728.3105
11 | Colour Washing Two Coats (GSI No. 26 (b) P-54). |  |  |  | P: % Sft: | 2335 | 859.9 | 20078.665
[7 empty] | TOTAL | 350292.9381
|  |  | CONTRACTOR | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD

## Distr...
BILL OF QUANTITIES
(A) Description and rate of Items based on Composite Schedule of Rates.
PART-B |  | REPAIR OF DISTRIBUTION SYSTEM
Item No. | Description of item to be executed at site | [5 empty] | Unit | Quantity | Rate | Amount in Rupees
1 | Excavation for pipe line in trenches and pits in soft soil i/c clay or mud trimming and dressing sides to true alignment shape leveling of beds of trenches to correct level & grade cutting joints holes i/c laying earth in 6” layers for construction of banks & banks dressing disposal of surplus earth within one chain as directed by Engineer Incharge providing fence guards lights flags temporary crossing for non vehicular traffic where ever required lift upto 5’ft: and lead upto one chain (PHSI No: 1 P-60) | [5 empty] | P: %0 Cft: | 3200 | 3600 | 11520
2 | Excavation for pipe line in trenches and pits in Wet soil i/c clay or mud trimming and dressing sides to true alignment shape leveling of beds of trenches to correct level & grade cutting joints holes i/c laying earth in 6” layers for construction of banks & banks dressing disposal of surplus earth within one chain as directed by Engineer Incharge providing fence guards lights flags temporary crossing for non vehicular traffic where ever required lift upto 5’ft: and lead upto one chain (PHSI No: 14 P-66) | [5 empty] | P: %0 Cft: | 1600 | 5400 | 8640
3 | Providing Laying Jointing PVC Pipe of class ‘B’ fixing in trenches i/c cutting fitting jointing with “Z” joint with one rubber Ring i/c testing with water to head of 61 meter or 200 ft: (PHSI No. 1 P-22).
|  |  |  | (i) | 6" dia |  | P: Rft: | 200 | 262 | 52400
|  |  |  | (ii) | 4" dia |  | P: Rft: | 190 | 137 | 26030
|  |  |  | (iii) | 3" dia |  | P: Rft: | 250 | 90 | 22500
4 | Supplying of PVC specials for PVC pipe (standard-weight) for PVC pipe ‘B’ class (SMI No. 10 P-12)
|  |  |  | (i) | G. Joint 6" dia |  | Each | 4 | 1062.5 | 4250
|  |  |  | (ii) | G. Joint 4" dia |  | Each | 8 | 731.25 | 5850
|  |  |  | (iii) | G. Joint 3" dia |  | Each | 10 | 568.75 | 5687.5
5 | Refilling the excavated stuff in 6” thick layers watering ramming to full compaction etc complete (PHSI No: 24 P-77) | [5 empty] | P: %0 Cft: | 4320 | 2760 | 11923.2
[9 empty] | TOTAL | 148800.7
|  |  | CONTRACTOR |  |  | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD

## P.M
BILL OF QUANTITIES
(A) Description and rate of Items based on Composite Schedule of Rates.
PART-C |  | PUMPING MACHINERY
Item No. | Description of item to be executed at site | [5 empty] | Unit | Quantity | Rate | Amount in Rupees
1 | Supplying & installing in position i/c transportation to site of work @ @ Water Works Qurban Shaheed Rind electric pumping set consisting of A.C electric motor 10 BHP 3 Phase 50 cycle 400/420 volts of 2900 RPM Siemens made type (ILA7-131-2AA-60) coupled with KSB pump type ETA (50-160) size 2 1/2“ x 2" mounted on common steel frame or base plate capable of discharge 120 gpm against the head of 90 ft: i/c installing of pumping set on cement concrete foundation Ratio (1:2:4) and C.C Ratio (1:4:8) with ballast with M.S nuts and bolts of 5/8” dia to be embedded in C.C foundation i/c providing and fixing automatic start delta starter (KSB) i/c providing & fixing prepared circuit breaker and neutral switch fuse with requireable type fuse link carrier 500 volts and 0-50 ampars installed on metaled board i/c providing internal electric wiring for main switch with 3-7/0.58 (10mm) PVC insulated wire 660 volts grade in 25 mm (1”) PVC conduit on surface as required i/c providing and fixing earthing with set with 0.6m x 0.6m x 6.3 mm (2 x 2 x ½ “) copper plate buried in ground at a depth 12" or less if water comes out from the ground level with salt and charcoal etc i/c making the pit 12" deep by excavation of all type of soil, earth plate to be connceted with No. S.S.W.G bare copper wire run in 1/2" G.I Pipe straight from the earth plate & testing of the pumping set against the required head of 72 hours etc complete (R.A Attached). | [5 empty] | Set | 1 | 282648 | 282648
2 | C.I Reflex valve heavy pattern (Test pressure) 21 kg per sq: or 300 Lbs:/ Sq: inch (SMI No. 6 (b) P-12)
[6 empty] | 6" dia | Each | 2 | 4062.5 | 8125
3 | C.I Sluice valve heavy pattern (Test pressure) 21 kg per sq: or 300 Lbs:/ Sq: inch (SMI No. 2 (b) P-12)
[6 empty] | 6" dia | Each | 2 | 9360 | 18720
4 | Providing, Laying & Fixing in trench i/c fitting, jointing & testing etc complete in all respect the high Density Polyethylene P.E pipes (HDPE-100) for W/S confirming ISO 4427/DIN8074 /8075 B.S 3580 & PSI 3051 (PHSI No. F (i) P-25)
| (90 mm) | For suction |  |  |  | 3" dia | P: Rft: | 36 | 148 | 5328
| (160 mm) | For delivery |  |  |  | 6" dia | P: Rft: | 24 | 440 | 10560
5 | C.I Foot valve heavy pattern with cone type gate (Imported) (SMI No. 4 P-12)
[6 empty] | 3" dia | Each | 2 | 731.25 | 1462.5
6 | C.I Bend with flanged and with holes i/c turning and facing of flanges for all sizes (PHSI No. 8 P-12)
[5 empty] | Bend 90 |  | P: Kg | 58.36 | 120 | 7003.2
7 | C.I Tee flanged and with holes i/c turning and facing of flanges for all size (PHSI No. 12 P-13)
[6 empty] | 3" dia | P: Kg | 25 | 120 | 3000
8 | Supplying of C.I specials for A.C pressure pipe (standard-weight) for ACIL ‘B’ class (SMI No: 9 P-15)
|  |  |  | Tail Piece 3" dia |  |  | Each | 8 | 375 | 3000
|  |  |  | Tail Piece 4" dia |  |  | Each | 8 | 618.75 | 4950
9 | C.I Tappers flat bottomed or central tapper flanged ends with hole i/c turning & fixing for all sizes (SMI No. 9 P-12)
[7 empty] | P: Kg | 50 | 120 | 6000
10 | Jointing C.I.M.S Flanged pipe and specials flanged and inside a trenches nuts and bolts with washer etc and other is required for joining and testing joints to the specified pressure etc complete (PHSI No.1 P-40)
[6 empty] | 3" dia | P: Joint | 12 | 499 | 5988
[6 empty] | 4" dia | Each | 13 | 513 | 6669
[9 empty] | TOTAL | 368979
|  |  | CONTRACTOR |  |  |  | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD

## R.PM
BILL OF QUANTITIES
(A) Description and rate of Items based on Composite Schedule of Rates.
PART-D |  | REPAIR OF PUMPING MACHINERY
Item No. | Description of item to be executed at site | [5 empty] | Unit | Quantity | Rate | Amount in Rupees
1 | Rewinding of Electric Motor 3 phase, 400/440 volts, 50 cycles with best quality insolated copper wire of required gauge i/c testing on load with satisfactory result upto one week's time, opening and refitting and replacing the bolts if necessary excluding the cost of worn out material (GSI No. 97 P-111)
[6 empty] | 10 BHP | Sets | 1 | 10141 | 10141
2 | Repair of Pump size 2" x 2 1/2" i/c turning facing of shaft and replacement of ball bearing body bush etc complete (M.R) | [5 empty] | Each | 1 | 10000 | 10000
3 | Motor control unit Automatic Star delta Starter consists of circuit breaker, magnetic contractor over load protection, under/ over voltage protection, phase failure protection Ammeter with current transformer voltmeters with potential transformer automatic star delta charge over switch, control and power cables indicating lights and all these components are fixed in a metallic dust and smoke proof box (M.R) (MEECO PAK) | [5 empty] | Each | 1 | 24800 | 24800
4 | Providing internal electric wiring for main switch 3-7/0.52 (10mm) PVC insulated wire 660 volts grade in 25 mm (1”) PVC conduit on surface as required (ESI No. 30 P-3). | [5 empty] | Meter | 16 | 606 | 9696
5 | C.I Sluice valve heavy pattern (Test pressure) 21 kg per sq: or 300 Lbs:/ Sq: inch (SMI No. 2 (b) P-12)
[6 empty] | 6" dia | Each | 2 | 9360 | 18720
[9 empty] | TOTAL | 73357
| Total Part-A |  | Rs. | 350293
| Total Part-B |  | Rs. | 148801
| Total Part-C |  | Rs. | 368979
| Total Part-D |  | Rs. | 73357
| TOTAL (a) |  | Rs. | 941430
--------- | % above/ below on the rates of CSR. |  |  |  | Amount to be added/ deducted on the basis of
[5 empty] | of premium quoted |  |  | Total (b) | _______________
Total (A) = a + b in words & figures
|  | CONTRACTOR |  |  |  | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD