## Civil Struc..
BILL OF QUANTITIES
(A) Description and rate of Items based on Composite Schedule of Rates.
Name of Work |  | REPAIR OF CIVIL STRUCTURE , PUMPING MACHINERY & SUPPLYING, INSTALLING & TESTING NEW PUMPING MACHINERY 7.5 BHP ( 1SET) FOR RURAL DRAINAGE SCHEME GHANDIA TALUKA SAKRAND DISTRICT SHAHEED BENAZIR ABAD
PART-A |  | REPAIR OF CIVIL STRUCTURE
Item No. | Description of item to be executed at site |  |  | Unit | Quantity | Rate | Amount
1 | Dismentling cement concrete plain (1:2:4) (GSI No. 19 P-10) |  |  | P:%0 Cft: | 45.74 | 3327.5 | 152.1998
2 | Pacca brick work (1:6) in other than building in cement, sand, mortar (GSI No. 7 P-21) |  |  | P:% Cft: | 42.19 | 12346.65 | 5209.0516
3 | Cement, Plaster (1:4) 1/2" thick up to 12’ height (GSI No.11 P-51) |  |  | P:% Sft: | 111.25 | 2283.93 | 2540.8721
4 | R.C.C work in roof slab beams columns rafts lintels and other structural members laid in situ or prrecast laid in position complete in all respect. (I) Ratio 2:2:4 Lbs cement2 Cft, sand 4 cft shingle1/8” to ¼” gauge (GSI No. 6 P-16) |  |  | P: Cft: | 45.74 | 337 | 15414.38
5 | Fabrication of mild steel reinforcement for C.C i/c cutting, bending, laying in position making joints and fastening i/c cost of binding wire (also i/c removal of rust from bars) (GSI No. 8 P-16) |  |  | P: Cwt: | 1.84 | 5001.7 | 9192
[6 empty] | TOTAL | 32507
|  |  | CONTRACTOR | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD

## De-silting
BILL OF QUANTITIES
(A) Description and rate of Items based on Composite Schedule of Rates.
PART-B |  | DE-SILTING OF SURFACE DARINS
Item No. | Description of item to be executed at site |  |  | Unit | Quantity | Rate | Amount in Rupees
1 | Earth work excavation in ASHES and soft soil or silt clearance undressed lead upto 50' ft: (GSI No. 2 P-1) |  |  | P: %0 Cft: | 4440.03 | 1663.75 | 16595
2 | Cleaning of Collecting Tank/ Sump Well below ground level i/c dewatering of sullage water and disposal of garbage solid waste etc outside the tank etc complete (PHSI No: 1 P-67) |  |  | P: %0 Cft: | 768 | 11900 | 9139.2
3 | Extra for every 50 ft: additional lead or part thereof for earth work (soft ordinary hard and very hard) (CSI No. 8 P-3) |  |  | P: %0 Cft: | 768 | 5039 | 3869.952
[6 empty] | TOTAL | 29604.152
|  | CONTRACTOR | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD

## P.Mach
BILL OF QUANTITIES
(A) Description and rate of Items based on Composite Schedule of Rates.
PART-C |  | PUMPING MACHINERY 7.5 BHP (1 SET)
Item No. | Description of item to be executed at site | [5 empty] | Unit | Quantity | Rate | Amount in Rupees
1 | Supplying & installing in position i/c transportation to site of work @ Village Ghandia electric pumping set consisting of A.C electric motor 7.5 BHP Siemens made 3 Phase 50 cycle 400/420 volts of 1450 RPM made type (ILA7-113-4AA-60) coupled with KSB non-clogging pump type KWPZ (65-315) size 3“ x 2 1/2” mounted on common steel frame or base plate capable of discharge 165 gpm against the head of 40 ft: i/c installing of pumping set on cement concrete foundation Ratio (1:2:4) and C.C Ratio (1:4:8) with ballast with M.S nuts and bolts of 5/8” dia to be embedded in C.C foundation i/c Supplying & fixing Automatic Motor Control Unit (MCU) consist oil starter (MEECO Pakistan) MCCB Breaker 10-A to 50-A (Shihlin Taiwan) cutout 60-A (China) amp meter (60-A) (SELCO China) volt meter (600-V) (SELCO China) phase indication light (China) include transformer oil (2 liters) panel board 18" x 26" x 9" and internal wiring etc complete i/c providing internal electric wiring for main switch with 3-7/0.52 (10mm) PVC insulated wire 660 volts grade in 25 mm (1”) PVC conduit on surface as required i/c providing and fixing earthing with set with 0.6m x 0.6m x 6.3 mm (2 x 2 x ½ “) G.I plate buried in ground at a depth of 3.7 m (12 ft:) for base plate & testing of the pumping set against the required head of 72 hours etc complete (R.A attached). | [5 empty] | P:Set | 1 | 664700 | 664700
2 | C.I Reflex valve heavy pattern (Test pressure) 21 kg per sq: or 300 Lbs:/ Sq: inch (SMI No. 6 (b) P-12)
[6 empty] | 3" dia | Each | 1 | 1543.75 | 1543.75
3 | C.I Sluice valve heavy pattern (Test pressure) 21 kg per sq: or 300 Lbs:/ Sq: inch (SMI No. 2 (b) P-12)
[6 empty] | 3" dia | Each | 1 | 4290 | 4290
4 | Manufacturing installing M.S Pipe 3" & 4" made out M.S sheet 3/16” (4.8 mm thick) i/c cutting folding proper curvature shape i/c welding etc complete (R.A approved Based on Schedule rates)
|  |  | For suction |  |  | 3" dia | P: Rft: | 16 | 385.89 | 6174.24
5 | Providing, Laying & Fixing in trench i/c fitting, jointing & testing etc complete in all respect the high Density Polyethylene P.E pipes (HDPE-100) for W/S confirming ISO 4427/DIN8074 /8075 B.S 3580 & PSI 3051 (PHSI No. F (i) P-25)
| (90 mm) | For suction & delivery |  |  |  | 3" dia | P: Rft: | 46 | 178 | 8188
6 | Manufacturing installing M.S Flanged 3/8” (12 mm thick) M.S sheet of required size drilling holes i/c cutting bending to correct shape welding etc complete (R.A approved Based on Schedule rates)
[6 empty] | 3" dia | Each | 14 | 500.89 | 7012.46
7 | C.I Foot valve heavy pattern with cone type gate (Imported) (SMI No. 4 P-12)
[6 empty] | 3" dia | Each | 1 | 731.25 | 731.25
8 | C.I Bend with flanged and with holes i/c turning and facing of flanges for all sizes (PHSI No. 8 P-12)
[5 empty] | Bend 90 3" dia |  | P: Kg | 33.4 | 120 | 4008
9 | C.I Tee flanged and with holes i/c turning and facing of flanges for all size (PHSI No. 12 P-13)
[6 empty] | 3" dia | P: Kg | 11.45 | 120 | 1374
10 | Supplying of C.I specials for A.C pressure pipe (standard-weight) for ACIL ‘B’ class (SMI No: 9 P-15)
|  |  |  | Tail Piece 4" dia |  |  | Each | 1 | 487.5 | 487.5
11 | C.I Tappers flat bottomed or central tapper flanged ends with hole i/c turning & fixing for all sizes (SMI No. 9 P-12)
|  |  |  | Reducer 2 1/2" x 3" |  |  | P: Kg | 10.5 | 120 | 1260
12 | But fusion Joint (PHS Mat: No. 1 P-21)
[6 empty] | 3" dia | Each | 10 | 600 | 6000
13 | Flange Adopter (M.R)
[6 empty] | 3" dia | Each | 10 | 675 | 6750
14 | Jointing C.I.M.S Flanged pipe and specials flanged and inside a trenches nuts and bolts with washer etc and other is required for joining and testing joints to the specified pressure etc complete (PHSI No.1 P-40)
[6 empty] | 3" dia | P: Joint | 20 | 499 | 9980
[9 empty] | TOTAL | 722499.2
|  |  | CONTRACTOR |  |  |  | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD

## R.PM
BILL OF QUANTITIES
(A) Description and rate of Items based on Composite Schedule of Rates.
PART-D |  | REPAIR OF PUMPING MACHINERY
Item No. | Description of item to be executed at site | [5 empty] | Unit | Quantity | Rate | Amount in Rupees
1 | Rewinding of Electric Motor 3 phase, 400/440 volts, 50 cycles with best quality insolated copper wire of required gauge i/c testing on load with satisfactory result upto one week's time, opening and refitting and replacing the bolts if necessary excluding the cost of worn out material (GSI No. 97 P-111)
[6 empty] | 5.5 BHP | Sets | 1 | 6610 | 6610
2 | Repair of Pump size 2" x 2 1/2" i/c turning facing of shaft and replacement of ball bearing body bush etc complete (M.R) | [5 empty] | Each | 1 | 10000 | 10000
[9 empty] | TOTAL | 16610
| Total Part-A |  | Rs. | 32507
| Total Part-B |  | Rs. | 29604
| Total Part-C |  | Rs. | 722499
| Total Part-D |  | Rs. | 16610
| TOTAL (a) |  | Rs. | 801220
--------- | % above/ below on the rates of CSR. |  |  |  | Amount to be added/ deducted on the basis of
[5 empty] | of premium quoted |  |  | Total (b) | _______________
Total (A) = a + b in words & figures
|  | CONTRACTOR |  |  |  | EXECUTIVE ENGINEER PUBLIC HEALTH ENGG: DIVISION SHAHEED BENAZIR ABAD