## Elect
BOQs
FOR CONSTRUCTION OF NEW NOORI GIRLS HOSTEL
AT
CMC LARKANA
2 (C) SCHEDULE OF ITEM (C), ELECTRICAL WORKS
S.No | Description of Item | Unit | Quantity | Rate | Amount
|  |  |  | (Rs.) | (Rs.)
1 | Wiring for light or fan point with 3/.029 PVC insulated wire in 20mm (3/4") PVC conduit recessed in the wall or column as required (S.NO.124,P.NO.15) SR-2012 | Point | 800 | 1130 | 904000
2 | Providing and laying (MAIN or SUB MAIN )PVC insulated with size 2-7/.029 Copper conductor in 3/4" dia PVC conduit recessed in the wall or column as required (S.NO.10, P.NO.2) SR-2012 | Meter | 8000 | 222 | 1776000
3 | Wiring for plug point with 3/.029 PVC insulated wire in 20mm (3/4") conduit recessed in the wall or column as required (S.NO.126,P.NO.15) SR-2012 | Point | 300 | 985 | 295500
4 | Providing & fixing three pin 5 amp plug & socket switch flush type on metal board & covered with plastic sheet (S.No-226, Pg-33) SR-2012 | No | 300 | 151 | 45300
5 | Wiring for call bell point with 3/.029 PVC insulated wire in 20mm (3/4") PVC conduit recessed in the wall or column as required (S.NO.128,P.NO.15) SR-2012 | Point | 1 | 1764 | 1764
6 | Providing & fixing bakelite / plastic ceiling rose with two terminals (S.No-228, Pg-33) SR-2012 | No | 99 | 72 | 7128
7 | Providing & fixing ceiling fan 56" good quality (S.No-235 Pg-34) SR-2012 | No | 130 | 3185 | 414050
8 | Providing & laying (Main or Submain) PVC insulated & PVC sheeted with 4 core copper conductor 600/1000 volts size 185mm2 (S.No-110 Pg-13) SR-2012 i.e. From (Concealed) Supply Point to MDB Hostel Building | Meter | 100 | 12478 | 1247800
9 | Providing & laying (Main or Submain) PVC insulated & PVC sheeted with 4 core copper conductor 600/1000 volts size 120mm2 (S.No-108 Pg-13) SR-2012 i.e From (Concealed) supply point to MDB 500A | Meter | 100 | 8175 | 817500
10 | Providing & laying (Main or Submain) PVC insulated & PVC sheeted with 4 core copper conductor 600/1000 volts size 16mm2 (S.No-102 Pg-12) SR-2012 i.e From (Concealed) MDBGF to DB1 > DB2GF and from MDBFF to DB, DB2FF) | Meter | 150 | 1300 | 195000
Total |  |  |  |  | 5704042
4C) NON SCHEDULE OF ITEM (C), ELECTRICAL WORKS
1 | Providing & laying ( Main or Submain ) PVC insulated with size 4-7 / 052 (10mmsq) copper conductor in 1 1/2" dia PVC conduit recessed in the wall or column i/c 4mmsq PVC insulated wire as ECC. As required ( from MDBGF to DB4 > DB6GF and from MDBFF to DB4FFDB5FF ) | Meter | 130
2 | Providing & laying ( Main or Submain ) PVC insulated with size 4-7 / 044 (6mmsq) copper conductor in 1 1/4" dia PVC conduit recessed in the wall or column i/c 2.5mmsq PVC insulated wire as ECC. As required ( from MDBGF to DB > DB6GF and from MDBFF to DB3FF & DB6FF) | Meter | 170
3 | China Switches
a. | Providing & fixing 1 gang china sheet fixed on metal board recess in the wall or column including making connections | No. | 147
b. | Providing & fixing 2 gang china sheet fixed on metal board recess in the wall or column including making connections | No. | 70
c. | Providing & fixing 10A Multifunction china sheet fixed on metal board recess in the wall or column including making connections | No. | 200
d. | Providing & fixing 15A Multifunction china sheet fixed on metal board recess in the wall or column including making connections | No. | 50
e. | Providing & fixing 1 Gang 2 Way china sheet fixed on metal board recess in the wall or column including making connections | No. | 12
f. | Providing & fixing Double 5 in 1 Universal Socket china sheet fixed on metal board recess in the wall or column including making connections | No. | 50
g. | Providing & fixing 4 gang 1 way china sheet fixed on metal board recess in the wall or column including making connections | No. | 8
h. | Providing & fixing 8 gang 1 way china sheet fixed on metal board recess in the wall or column including making connections | No. | 8
i. | Providing & fixing 10 gang 1 way china sheet fixed on metal board recess in the wall or column including making connections | No. | 12
j. | Providing & fixing Bell Push china sheet fixed on metal board recess in the wall or column including making connections | No. | 1
k. | Providing & fixing Single T.V china sheet fixed on metal board recess in the wall or column including making connections | No. | 2
l. | Providing & fixing Single Telephone china sheet fixed on metal board recess in the wall or column including making connections | No. | 2
4 | Corridor
a. | Providing and fixing wall bracket light fitting fancy type as approved by the engineer incharge. | No | 176
b. | Providing & fixing screw type batten holder supperior quality suitable for 12 watt LED lamp | No. | 539
c. | Providind & fixing LED lamp 12 watt 250 voold ( china make) | No. | 539
5 | Providing and fixing 4 1/2" x 4 1/2" MS dia casted powder coated recessed type fan clamp box with 3/8" dia MS bar fan clamp fixed on roof at casting time as required. | No | 130
6 | Providing and fixing 6 Amps Piano fan dimmer fixed on plastic or fiber top cover sheet on 14 SWG metal board recessed in the wall and column including connection as required. | No | 130
7 | Providing and fixing 30cm (12") sweep metallic body exhaust fan complete with blades, motor, shutter etc fitted in exisitng hole including connection with 14.0076 flexible wire complete as required Millat / Pak / Asia / Climax / Younas / Royal. | No | 25
8 | Providing and fixing Earthing set with 2'x2'x1/8'' copper plate buried in the ground at a depth of 12 feet or less if water comes out from the ground level (with salt and charcoal, or Earthing chamical Powder) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock) including fixing of 2x8 SWG copper wire in 1/2 '' G.I conduit complete in all respect as required. | Job | 1
9 | Providing & Fixing Classic Power Plug Porcelain Type (40A) Suitable for Split/ Window Air condition fixed on prepared board as required, complete in all respects (Recommended: Heavy, Hero or Equivalent). | Per No. | 15
10 | Providing & Fixing Bracket Fan by making all necessary connections to the available Ceiling Rose (Recommended: SK Fan or Equivalent Copper). | Per No. | 50
11 | Providing & Fixing LED Flood Light 100 Watss on movable Stand as required (Recommended: Orient, OSAKA or equivalent). | Per No. | 20
12 | Providing & Fixing Lawn/ Garedn/ Walk Way Fiber Pole (Double Arm) at the height of 8.5', 5" Dia including Fancy Globes/ Lights/ Covers hanged (Side by Side) on it including LED Light/ Saver of 37 Watts (Each) of good quality fixed on ground by excavation of any type of soil to the depth of 2' by concreting with ration 1:2:4 as per required size of the pole base with anchor nuts. bolts, wiring and back filling as required and approved by E.I, Complete in all respects | Per Job | 20
13 | Providing & Fixing A.C or D.C Electric Bell 200/250 volts by making all the necessary connections, Complete in all respects | No. | 1
14 | Providing & Fixing Capsule Lights of good Quality including Energy Saver (23 Watts) by making all the necessary connections alreadt laid at the location, Complete in all respects | No. | 30
15 | Main Distribution Board (GF)
| Providing and fixing testing, commissioning cubical type metal sheet main distribution board floor type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire including Bus Bars complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 1
Incoming:
1) 500 A TP MCCB 36 KA 1 No Terasaki/Similar
2) Volt Meter With Selector 1 No
3) Ampere Meter With Selector 1 No
4) CT 500/5A 3 No
5) Pilot Lamp 3 No
6) Control fuse 3 No.
Outgoing:
1) 250 A TP MCCB (DB1, DB3) 2 No Terasaki/Similar
2) 60 A TP MCCB (Spare) 1 No
3) 30 A TP MCCB (Spare) 1 No
16 | Main Distribution Board (GF)
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flush type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire including Bus Bars complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 1
Incoming:
1) 250 A TP MCCB 35 KA 1 No Terasaki/Similar
2) Volt Meter With Selector 1 No
3) Ampere Meter With Selector 1 No
4) CT 250/5A 3 No
5) Pilot Lamp 3 No
Outgoing:
1) 50 A TP MCCB (DB1, DB2, GF) 2 No Terasaki/Similar
2) 40 A TP MCCB (DB4, DB6 , GF) 2 No
3) 30 A TP MCCB (DB3, DB5,DB7 , GF) 3 No
3) 15 A TP MCCB (Spare) 1 No
17 | Main Distribution Board (FF)
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flush type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire including bus barss complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 1
Incoming:
1) 250 A TP MCCB 35 KA 1 No Terasaki/Similar
2) Volt Meter With Selector 1 No
3) Ampere Meter With Selector 1 No
4) CT 250/5A 3 No
5) Pilot Lamp 3 No
Outgoing:
1) 50 A TP MCCB (DB1, FF, DB2, FF) 2 No Terasaki/Similar
2) 40 A TP MCCB (DB4, FF, DB5 , FF) 2 No
3) 30 A TP MCCB (DB3, FF, DB6,FF) 2 No
3) 15 A TP MCCB (Spare) 1 No
18 | DB1 FF
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flus type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire including bus bars complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 1
Incoming:
1) 50 A TP MCCB (5 KA) 1 No Terasaki/Similar
2) Pilot Lamp 3 No
Outgoing:
1) 10 A SP MCB 8 No Terasaki/Similar
2) 15 A SP MCB 10 No
25/30 A SP MCB 04 No.
10 A SP MCB (spare) 01 No.
19 | DB2 GF
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flush type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 1
Incoming:
1) 20 A TP MCCB (5 KA) 1 No Terasaki/Similar
2) Pilot Lamp 3 No
Outgoing:
1) 10 A SP MCB 8 No Terasaki/Similar
2) 15 A SP MCB 1 No
3) 10 A SP MCB (Spare) 1 No
20 | DB3 GF
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flush type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 1
Incoming:
1) 50 A TP MCCB (5 KA) 1 No Terasaki/Similar
2) Pilot Lamp 3 No
Outgoing:
1) 10 A SP MCB 28 No Terasaki/Similar
2) 10 A SP MCB (Spare) 2 No
21 | DB1 FF
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flush type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 1
Incoming:
1) 50 A TP MCCB (5 KA) 1 No Terasaki/Similar
2) Pilot Lamp 3 No
Outgoing:
1) 10 A SP MCB 8 No Terasaki/Similar
2) 15 A SP MCB 10 No
3) 25/30 A SP MCB 4 No
3) 10 A SP MCB (Spare) 1 No
22 | DB2 FF
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flush type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire wire including bus bar complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 1
Incoming:
1) 50 A TP MCCB 1 No Terasaki/Similar
2) Pilot Lamp 3 No
Outgoing:
1) 10 A SP MCB 9 No Terasaki/Similar
2) 15 A SP MCB 4 No
3) 25/30 A SP MCB 5 No
4) 10 A SP MCB (Spare) 3 No
23 | DB4 GF DB6 G.F, DB4 FF, DB5 FF
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flush type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 4
Incoming:
1) 40 A TP MCCB 1 No Terasaki/Similar
2) Pilot Lamp 3 No
Outgoing:
1) 10 A SP MCB 8 No Terasaki/Similar
2) 15 A SP MCB (PP) 4 No
3) 25/30 A SP MCB (AC) 4 No
4) 10 A SP MCB (Spare) 1 No
24 | DB5 GF
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flush type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 1
Incoming:
1) 30 A TP MCCB 1 No Terasaki/Similar
2) Pilot Lamp 3 No
Outgoing:
1) 10 A SP MCB 10 No Terasaki/Similar
2) 15 A SP MCB (PP) 1 No
3) 25/30 A SP MCB (AC) 5 No
4) 10 A SP MCB (Spare) 2 No
25 | DB1 & DB2 GF, DB1 FF, DB2 FF
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flush type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire including bus bar complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 4
Incoming:
1) 50 A TP MCCB 1 No Terasaki/Similar
2) Pilot Lamp 3 No
Outgoing:
1) 10 A SP MCB 10 No Terasaki/Similar
2) 15 A SP MCB (PP) 4 No
3) 25/30 A SP MCB (AC) 5 No
4) 10 A SP MCB (Spare) 2 No
26 | DB3, DB7 GF, DB3 FF, DB6 FF
| Providing and fixing testing, commissioning cubical type metal sheet distribution board flush type with locking arrangement duly powder quoted paint including all fastening material including wiring with suitable gauge PVC x PVC wire including bus bar complete in all respect (Pel, Libra, RCO, Karimi, Electromech System, In Power Tech, Global Tech). | No | 4
Incoming:
1) 30 A TP MCCB 1 No Terasaki/Similar
2) Pilot Lamp 3 No
Outgoing:
1) 10 A SP MCB 8 No Terasaki/Similar
2) 15 A SP MCB (PP) 3 No
3) 25/30 A SP MCB (AC) 3 No
4) 10 A SP MCB (Spare) 1 No
Total Rs.