Part (F) Pumping Machinery (At Water Works)

- Supplying and installing in position i/c transportation to site of Improvement Extension & Change Source Water Supply Scheme Hingorno From Mithrao Canal Electric Pumping set of 2900 RPM (Siemens) made 30 BHP Electric motor 3 phase 50 Cycle 400/420 volts with centrifugal pump type ETA-80-20, size 4”x3”   mounted on commons steel frame on base plate (capable of discharge 425 GPM against the required head of 170 ft, i/c installed on cement concrete ratio 1:2:4 Ms nuts bolts of 5/8” dia to be embedded in cement concrete foundation providing fixing MCU star delta starter (Siemens  made) made and providing internal electric wiring for main switch 3-7/0.44” (1”     ) dia PVC insulated wire 660 volts grade (i) buried on the ground at depth of 3.7 m (12 ft) as per Pak PWD specifications and testing pumping set against the required head for 72 hours etc complete (R.A attached).

2.00 Set		@ Rs. 527570/-  		P.Set		Rs. 1055140/-

2.	Manufacturing and installing 3” dia & 4” dia  M.S pipe made out of M/S sheet (3/16”) thick M.S sheet i/c cutting bending folding to correct curvature as shape (R.A attached).

(i) Suction 6” Dia

42.0 Rft		@ Rs.749/34			P.Rft		Rs. 31472/-

(ii) Delivery 6” Dia

20.00 Rft		@ Rs.749/34			P.Rft		Rs. 14987-

3.	Manufacturing Supplying M.S flanges (PHSI No.1 P-32)

6” Dia

12.00 Nos		@ Rs. 804/77			Each		Rs. 9657/-

6” Dia

6.00 Nos		@ Rs. 804/77			Each		Rs. 4829-

4.	C. I sulice valve heavy pattern (test pressure 300 lbs/sq: inch) SOMI No. 2 P-09).

6” Dia

2.00 Nos		@ Rs. 5460/- 			Each		Rs. 10920/-

5.	C.I reflex valve heavy pattern (test pressure 300 lbs/square inch (SMOI No. P-10).

6” Dia

2.00 Nos		@ Rs. 1706/25		Each		Rs. 3413/-

6.	C.I foot valve heavy pattern with cone type gate (imported) (SOMI No. 4 P-10).

6” Dia

2.00 Nos		@ Rs. 1381/25		Each		Rs. 2763/-

7.	C. I bend with flanged ends with holes i/c turning and facing of flanges for all size (SOMI No. 8 P-11).

6” Dia 90*

93.05 Kg		@ Rs. 	120/-			P. Kg		Rs. 11166/-

8.	C. I tappers flat bottomed or central tapered flanged ends with holes i/c turning and facing of flanges for all sizes (SOMI No. 9 P-11).

6x6

59.20 KG		@ Rs. 120/-			P. Kg		Rs. 7104/-

9.	C.I tee with flanged ends with holes i/c turning and facing of flanges for all sizes (SOMI No. 7 P-11).

Tee 6” x 6”

23.86 Kg		@ Rs. 120			P. Kg		Rs. 2863/-

10.	C.I Short piece (SOMI No. 9 P-15).

6” Dia

1.00 No		@ Rs. 618/75			Each		Rs. 618/-

11.	Jointing C.I/M.S flanged pipes and specials flange and inside a trench i/c supplying rubber packing of the required thickness nuts bolts with washers etc and other tools required for jointing and testing the joint to the specified pressure etc complete (PHSI No. 1 P-35).

(i) 6” Dia

12.00 Joint		@ Rs.938/-			P. Joint	Rs. 22512/-

12.	Painting New surface

Preparing surface and painting of filled framing skirting pipes gutters similar lincar work not exceeding 4” inch (GSI No. 4 P-75).

62.00 Rft		@ Rs. 686/95			P % Rft	Rs. 426/-

13.	Cutting holes 4”x6” in stone masonry or brick wall with repairing machinery  within (GSI No.72 P-106).

3.0 Nos.		 @ Rs.169/40 			P. Hole	Rs.508 ____  										Total: -	Rs.1170188/-

=========